## Request a quote
Request a quotation for DEH 12–36kV Pipeline
Share rated voltage (1.0 kV to 220 kV), phase cross-section, optical fibre count, water depth / pulling tension and continuous delivery length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/deh-12-36kv-subsea-pipeline-heating-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
DEH 12–36 kV AC Single-Core Subsea Pipeline Direct Electrical Heating – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/deh-12-36kv-subsea-pipeline-heating-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Breaking / tensile kN ≈ | Min. bend R mm | Series
| DEH 12–36kV Pipeline Config A | 3×25–50 mm² (or 3P+FO Composite) | Compacted / Class 5 Cu/SnCu + FO | 32 | 1850 | 85 | 380 | DEH 12–36kV Pipeline Construction Schedule (−20…+90 °C)
| DEH 12–36kV Pipeline Config B | 3×95–150 mm² (or Heavy EOM) | Compacted / Class 5 Cu/SnCu + FO | 48.5 | 4280 | 130 | 580 | DEH 12–36kV Pipeline Construction Schedule (−20…+90 °C)
| DEH 12–36kV Pipeline Config C | 3×240–400 mm² (or Trunk HV/MV) | Compacted Cu + Lead/Armour + FO | 78 | 9650 | 210 | 950 | DEH 12–36kV Pipeline Construction Schedule (−20…+90 °C)
Custom core cross-sections, pair/fibre counts, armour breaking loads and continuous winch/seabed lengths available per DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification.

## Electrical, optical & thermal p
DEH 12–36 kV AC Single-Core Subsea Pipeline Direct Electrical Heating – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/deh-12-36kv-subsea-pipeline-heating-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3×25–50 mm² (or 3P+FO Composite) | 0.495 | 12 kV – 36 kV (Subsea/MV) | −20…+90 °C
3×95–150 mm² (or Heavy EOM) | 0.193 | 12 kV – 36 kV (Subsea/MV) | −20…+90 °C
3×240–400 mm² (or Trunk HV/MV) | 0.075 | 12 kV – 36 kV (Trunk/HV) | −20…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
DEH 12–36 kV AC Single-Core Subsea Pipeline Direct Electrical Heating – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/deh-12-36kv-subsea-pipeline-heating-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 12 kV – 36 kV (Tested per DNV-RP-F104 / IEC 60502-2 DEH)
Key data | Operating temp. | −20…+90 °C (Continuous subsea & offshore service)
Key data | Min. bend radius | 15 × OD (Winch sheave, chute & seabed routing)
Key data | Core / conductor | Large-Section Fl (High-current stranded copper core for pi)
Key data | Outer protection | Non-Magnetic Sta (Low-loss non-magnetic wire armour for si)
Key data | Standard | DNV-RP-F104 / IE (DNV-RP-F104 & IEC 60502-2 12–36 kV Subse)
Electrical | Rated voltage / transmission duty | 12 kV – 36 kV (DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification)
Electrical | Core / conductor construction | Large-Section Flexible Copper Conductor (1/C) — High-current stranded copper core for pipeline electrical heating
Electrical | Primary dielectric / buffering | 12-36 kV Triple-Extruded XLPE Insulation — Conductor screen + HV XLPE dielectric + insulation screen
Thermal | Continuous operating temperature | −20…+90 °C (subsea & offshore duty)
Thermal | Hydrostatic & thermal stability | Verified thermal and hydrostatic stability per DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel winch reel
Mechanical | Outer protection / armouring | Non-Magnetic Stainless-Steel / Copper Armour — Low-loss non-magnetic wire armour for single-core AC operation
Mechanical | Minimum bending radius | 15 × OD
Mechanical | Armour, strength member & mechanical duty | Semi-Conducting Polyethylene (PE) Sheath — Extruded semi-conducting PE jacket allowing capacitive seawater transfer
Resistance | Seawater, hydrostatic & hydrolysis resistance | Engineered for continuous seawater immersion, pressure cycling and hydrolysis resistance per DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification
Resistance | Oil, drilling mud & abrasion resistance | Resistant to marine hydraulic oils, salt mist, winch sheave wear and seabed abrasion per DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification
Standards | Environmental & test standards | IEC 60228 / IEC 60794 / ITU-T G.972 / IEEE 1580 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | DEH 12–36kV Pipeline
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Non-Magnetic Sta)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
DEH 12–36 kV AC Single-Core Subsea Pipeline Direct Electrical Heating – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/deh-12-36kv-subsea-pipeline-heating-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Large-Section Flexible Copper Conductor | High-current stranded copper core for pipeline electrical heating
2 | 12-36 kV Triple-Extruded XLPE Insulation | Conductor screen + HV XLPE dielectric + insulation screen
3 | Semi-Conducting Polyethylene (PE) Sheath | Extruded semi-conducting PE jacket allowing capacitive seawater transfer
4 | Non-Magnetic Stainless-Steel / Copper Ar | Low-loss non-magnetic wire armour for single-core AC operation
| DEH 12–36kV Pipeline — Standard Subsea & Offshore Execution | Built to DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification with large-section flexible copper conductor (1/c) and non-magnetic stainless-steel / copper armour
| DEH 12–36kV Pipeline — Custom Continuous Winch / Reel Length | Available in custom continuous subsea winch, tow or seabed lengths with water-blocked terminations
| DEH 12–36kV Pipeline — Hydrostatic, Tensile & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, optical OTDR / DC resistance & tensile test report

## Quality and supply
DEH 12–36 kV AC Single-Core Subsea Pipeline Direct Electrical Heating – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/deh-12-36kv-subsea-pipeline-heating-cable/ ¦ Data revision 2026-10-26
Typical values for this cable type, based on DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, optical OTDR continuity & dimensional verification (DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification) — DC resistance at 20 °C / optical attenuation and outer diameter within DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification) — Zero dielectric breakdown and verified insulation resistance for 12 kV – 36 kV rating | Every manufactured drum length
Type test | Hydrostatic pressure, tensile breaking load & water-blocking qualification (DNV-RP-F104 & IEC 60502-2 12–36 kV Subsea Pipeline Direct Electrical Heating Specification) — Verified subsea pressure integrity, torque-balanced tensile performance and thermal stability across −20…+90 °C | Type qualification & periodic lot audit
Standard / approval | DNV-RP-F104 / IEC 60502-2 DEH Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX DEH 12–36kV Pipeline DNV-RP-F104 / IEC 60502-2 DEH 12 kV – 36 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel oceanographic winch reels or submarine turntables
Supply | Standard lengths: 500 m, 1,000 m, 3,000 m, 6,000 m or custom continuous subsea lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom subsea builds)
Supply | Lead time: 2–6 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP