## Request a quote
Request a quotation for DLO 2 kV
For traction motor jumpers, BESS rack interconnects or cable tray feeders, include the AWG/kcmil size, installation environment (raceway, open tray or flexing bogie drop) and required lug or reel lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/dlo-diesel-locomotive-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
DLO 2 kV Diesel Locomotive & Traction Power Cable – Dimensions & mass (21) (21)
TEBAOFLEX ¦ https://tebaoflex.com/cables/dlo-diesel-locomotive-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AAR RP-585 / ICEA S-95-658 / UL 44 Type RHH/RHW-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | AWG / kcmil | Cross-section (mm²) | Stranding (No./AWG) | Conductor OD (mm) | EPR wall (mm) | XL-CPE wall (mm) | Nominal OD (in) | Nominal OD (mm) | Copper mass (kg/km) | Total mass (lb/kft) | Total mass (kg/km)
| DLO 1×14 AWG (2.1 mm²) | 14 AWG | 2.08 | 19/27 | 1.8 | 1.14 | 0.76 | 0.2 | 5.1 | 20 | 32 | 48
| DLO 1×12 AWG (3.3 mm²) | 12 AWG | 3.31 | 19/25 | 2.3 | 1.14 | 0.76 | 0.22 | 5.6 | 32 | 39 | 58
| DLO 1×10 AWG (5.3 mm²) | 10 AWG | 5.26 | 27/24 | 3 | 1.14 | 0.76 | 0.25 | 6.4 | 50 | 53 | 79
| DLO 1×8 AWG (8.4 mm²) | 8 AWG | 8.37 | 37/24 | 3.7 | 1.52 | 0.76 | 0.31 | 7.9 | 80 | 78 | 116
| DLO 1×6 AWG (13.3 mm²) | 6 AWG | 13.3 | 61/24 | 4.8 | 1.52 | 1.14 | 0.39 | 9.9 | 127 | 135 | 201
| DLO 1×4 AWG (21.2 mm²) | 4 AWG | 21.15 | 105/24 | 6.4 | 1.52 | 1.14 | 0.45 | 11.4 | 202 | 195 | 290
| DLO 1×2 AWG (33.6 mm²) | 2 AWG | 33.62 | 154/24 | 7.9 | 1.52 | 1.14 | 0.51 | 13 | 321 | 275 | 409
| DLO 1×1 AWG (42.4 mm²) | 1 AWG | 42.41 | 224/24 | 9.5 | 2.03 | 1.14 | 0.62 | 15.7 | 405 | 390 | 580
| DLO 1×1/0 AWG (53.5 mm²) | 1/0 AWG | 53.49 | 275/24 | 10.6 | 2.03 | 1.14 | 0.66 | 16.8 | 511 | 465 | 692
| DLO 1×2/0 AWG (67.4 mm²) | 2/0 AWG | 67.43 | 325/24 | 11.6 | 2.03 | 1.14 | 0.7 | 17.8 | 644 | 540 | 804
| DLO 1×3/0 AWG (85.0 mm²) | 3/0 AWG | 85.01 | 450/24 | 13.5 | 2.03 | 1.14 | 0.78 | 19.8 | 812 | 715 | 1064
| DLO 1×4/0 AWG (107.2 mm²) | 4/0 AWG | 107.2 | 550/24 | 15 | 2.03 | 1.14 | 0.84 | 21.3 | 1024 | 860 | 1280
| DLO 1×262.6 kcmil (133 mm²) | 262.6 kcmil | 133.1 | 650/24 | 16.5 | 2.41 | 1.65 | 0.97 | 24.6 | 1271 | 1090 | 1622
| DLO 1×313.1 kcmil (159 mm²) | 313.1 kcmil | 158.6 | 775/24 | 18 | 2.41 | 1.65 | 1.03 | 26.2 | 1515 | 1285 | 1912
| DLO 1×373.7 kcmil (189 mm²) | 373.7 kcmil | 189.4 | 925/24 | 19.6 | 2.41 | 1.65 | 1.09 | 27.7 | 1809 | 1505 | 2240
| DLO 1×444.4 kcmil (225 mm²) | 444.4 kcmil | 225.2 | 1100/24 | 21.4 | 2.41 | 1.65 | 1.16 | 29.5 | 2151 | 1770 | 2634
| DLO 1×535.3 kcmil (271 mm²) | 535.3 kcmil | 271.2 | 1325/24 | 23.6 | 2.79 | 1.65 | 1.28 | 32.5 | 2590 | 2120 | 3155
| DLO 1×646.4 kcmil (328 mm²) | 646.4 kcmil | 327.5 | 1600/24 | 26 | 2.79 | 1.65 | 1.37 | 34.8 | 3128 | 2545 | 3787
| DLO 1×777.7 kcmil (394 mm²) | 777.7 kcmil | 394.1 | 1925/24 | 28.4 | 2.79 | 2.03 | 1.5 | 38.1 | 3764 | 3070 | 4569
| DLO 1×929.9 kcmil (471 mm²) | 929.9 kcmil | 471.2 | 2300/24 | 31.2 | 2.79 | 2.03 | 1.61 | 40.9 | 4500 | 3620 | 5387
| DLO 1×1111.1 kcmil (563 mm²) | 1111.1 kcmil | 563 | 2750/24 | 34.2 | 2.79 | 2.03 | 1.73 | 43.9 | 5377 | 4320 | 6429
Dimensions and masses are nominal production values per TEBAOFLEX datasheet TBF-DS-DLO-2KV-01 Rev 1.0 and ICEA S-95-658.
Sizes 1/0 AWG and larger are rated and marked 'For CT Use' (Cable Tray) and pass IEEE 1202 / FT4 (70,000 BTU/hr) vertical tray flame testing.

## Ampacity & test voltage
DLO 2 kV Diesel Locomotive & Traction Power Cable – Ampacity & test voltage (21) (21)
TEBAOFLEX ¦ https://tebaoflex.com/cables/dlo-diesel-locomotive-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AAR RP-585 / ICEA S-95-658 / UL 44 Type RHH/RHW-2. Values for your order are confirmed in the quotation.
Designation | AWG / kcmil | Cross-section (mm²) | 75 °C raceway (A) | 90 °C raceway (A) | 90 °C free air (A) | 5-min AC test (kV)
DLO 1×14 AWG (2.1 mm²) | 14 AWG | 2.08 | 20 | 25 | 35 | 6
DLO 1×12 AWG (3.3 mm²) | 12 AWG | 3.31 | 25 | 30 | 40 | 6
DLO 1×10 AWG (5.3 mm²) | 10 AWG | 5.26 | 35 | 40 | 55 | 6
DLO 1×8 AWG (8.4 mm²) | 8 AWG | 8.37 | 50 | 55 | 80 | 7.5
DLO 1×6 AWG (13.3 mm²) | 6 AWG | 13.3 | 65 | 75 | 105 | 7.5
DLO 1×4 AWG (21.2 mm²) | 4 AWG | 21.15 | 85 | 95 | 140 | 7.5
DLO 1×2 AWG (33.6 mm²) | 2 AWG | 33.62 | 115 | 130 | 190 | 7.5
DLO 1×1 AWG (42.4 mm²) | 1 AWG | 42.41 | 130 | 145 | 220 | 9
DLO 1×1/0 AWG (53.5 mm²) | 1/0 AWG | 53.49 | 150 | 170 | 260 | 9
DLO 1×2/0 AWG (67.4 mm²) | 2/0 AWG | 67.43 | 175 | 195 | 300 | 9
DLO 1×3/0 AWG (85.0 mm²) | 3/0 AWG | 85.01 | 200 | 225 | 350 | 9
DLO 1×4/0 AWG (107.2 mm²) | 4/0 AWG | 107.2 | 230 | 260 | 405 | 9
DLO 1×262.6 kcmil (133 mm²) | 262.6 kcmil | 133.1 | 275 | 310 | 485 | 11
DLO 1×313.1 kcmil (159 mm²) | 313.1 kcmil | 158.6 | 305 | 345 | 540 | 11
DLO 1×373.7 kcmil (189 mm²) | 373.7 kcmil | 189.4 | 340 | 385 | 600 | 11
DLO 1×444.4 kcmil (225 mm²) | 444.4 kcmil | 225.2 | 375 | 425 | 670 | 11
DLO 1×535.3 kcmil (271 mm²) | 535.3 kcmil | 271.2 | 420 | 475 | 760 | 11
DLO 1×646.4 kcmil (328 mm²) | 646.4 kcmil | 327.5 | 465 | 525 | 850 | 13.5
DLO 1×777.7 kcmil (394 mm²) | 777.7 kcmil | 394.1 | 510 | 575 | 960 | 13.5
DLO 1×929.9 kcmil (471 mm²) | 929.9 kcmil | 471.2 | 545 | 615 | 1045 | 13.5
DLO 1×1111.1 kcmil (563 mm²) | 1111.1 kcmil | 563 | 570 | 648 | 1119 | 13.5
Raceway ampacities are based on NEC (NFPA 70) Table 310.16 for not more than three current-carrying conductors in raceway, cable or earth at 30 °C ambient.
Free-air ampacities are based on single-conductor installation in free air at 30 °C ambient and 90 °C conductor temperature per NEC Table 310.17 / ICEA P-54-440.

## Technical data
DLO 2 kV Diesel Locomotive & Traction Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/dlo-diesel-locomotive-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AAR RP-585 / ICEA S-95-658 / UL 44 Type RHH/RHW-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage | 2,000 V (UL RHH/RHW-2 2 kV · CSA RW90 1 kV)
Key data | Conductor temp. | +90 °C (Wet or dry · +130 °C overload)
Key data | Cold bend | −40 °C (Cold bend & impact per UL 44)
Key data | Conductor | Class I / K (Tinned copper · 24 AWG strands)
Key data | Min. bend radius | 6 × D (Installed · 8 × D flexing duty)
Key data | Size range | 14 AWG–1111 (21 sizes · 2.1 to 563 mm²)
Electrical | Rated voltage | 2,000 V (UL RHH/RHW-2 600 V / 2 kV)
Electrical | CSA voltage rating | 1,000 V (CSA C22.2 No. 38 Type RW90)
Electrical | AC test voltage (5 min) | 6.0–13.5 kV AC by conductor size
Electrical | Spark test voltage | 7.5–15.0 kV AC RMS in-line
Thermal | Continuous conductor temp. | +90 °C wet or dry
Thermal | Emergency overload temp. | +130 °C
Thermal | Short-circuit temperature | +250 °C (5 s maximum)
Thermal | Cold bend temperature | −40 °C (UL 44 cold bend & impact)
Mechanical | Conductor stranding | 24 AWG (0.51 mm) tinned copper, Class I/K
Mechanical | Min. bend radius (fixed) | 6 × cable overall diameter
Mechanical | Min. bend radius (flexing) | 8 × cable overall diameter
Resistance | Flame retardance | UL 1581 VW-1; IEEE 1202 / FT4 (≥ 1/0 AWG)
Resistance | Mine flame acceptance | MSHA 30 CFR Part 7 flame resistance
Resistance | Oil & fluid resistance | UL 44 Oil Resistant I & II (60 °C / 75 °C)
Resistance | Sunlight & weather | UL 44 720-hour carbon-arc / xenon-arc UV
Standards | Locomotive & power | AAR RP-585 / S-501; ICEA S-95-658 (NEMA WC70)
Standards | North American listings | UL 44 Type RHH/RHW-2; CSA C22.2 No. 38 RW90
Standards | Conductor specification | ASTM B33 (tinned); ASTM B172 Class I / K
Identification | Outer sheath colour | Black heavy-duty XL-CPE (custom colours on request)
Identification | Cable tray & sunlight mark | For CT Use (≥ 1/0 AWG) · Sunlight Resistant
Identification | Surface legend | Hot-foil or white inkjet print at 2 ft intervals

## Construction
DLO 2 kV Diesel Locomotive & Traction Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/dlo-diesel-locomotive-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AAR RP-585 / ICEA S-95-658 / UL 44 Type RHH/RHW-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Extra-flexible tinned copper conductor | Annealed tinned copper, bunch or rope-lay stranded (24 AWG / 0.51 mm wires) per ASTM B33 and ASTM B172 Class I / Class K | ASTM B33 / ASTM B172
2 | Conductor separator tape | Non-hygroscopic polyester or paper separator tape promoting clean strip and strand flexing | ICEA S-95-658
3 | Thermoset EPR insulation | Flame-retardant ethylene propylene rubber (EPR), 90 °C wet/dry, meeting UL 44 Type RHH/RHW-2 and CSA RW90 | UL 44 / CSA C22.2 No. 38
4 | Heavy-duty XL-CPE outer jacket | Cross-linked chlorinated polyethylene (XL-CPE), black, thermoset, oil-, sunlight-, abrasion- and flame-resistant | ICEA S-95-658 / NEMA WC70
| DLO 2 kV Standard (EPR / XL-CPE) | Two-layer extruded thermoset EPR insulation with a separate heavy-duty black XL-CPE outer sheath and separator tape for clean lug stripping.
| DLO 2 kV CT Rated (1/0 AWG – 1111 kcmil) | Marked 'For CT Use' and IEEE 1202 / FT4 vertical tray flame rated for open ladder and ventilated industrial cable trays.

## Quality and supply
DLO 2 kV Diesel Locomotive & Traction Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/dlo-diesel-locomotive-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on AAR RP-585 / ICEA S-95-658 / UL 44 Type RHH/RHW-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & stranding verification — 100 % reel verification at 20 °C per ASTM B33 / ASTM B172 Class I & K | Every production length
Routine test | In-line AC spark & 5-minute dielectric withstand test — Spark test at 7.5–15.0 kV RMS; 5-min AC water-tank withstand at 6.0–13.5 kV by size per ICEA S-95-658 | Every production length
Routine test | Insulation resistance measurement — IR ≥ K × log10(D/d) with K ≥ 10,000 MΩ·1000 ft at 15.6 °C after AC voltage test | Every production length
Type test | Flame propagation (VW-1, IEEE 1202 / FT4 & MSHA) — UL 1581 VW-1 vertical flame, IEEE 1202 / FT4 70,000 BTU/hr vertical tray (≥ 1/0 AWG) and MSHA 30 CFR Part 7 | Type approval & periodic audit
Type test | Hot oil immersion & −40 °C cold bend / impact — UL 44 Oil Resistant I & II (60 d at 75 °C) and crack-free cold bend / impact at −40 °C | Type approval & periodic sample
Standard / approval | UL 44 Listed Type RHH / RHW-2 (600 V / 2,000 V, 90 °C wet/dry)
Standard / approval | CSA C22.2 No. 38 Certified Type RW90 (1,000 V, −40 °C, FT4)
Standard / approval | AAR RP-585 / S-501 & ICEA S-95-658 / NEMA WC70
Standard / approval | MSHA 30 CFR Part 7 Flame-Resistant Acceptance
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX — DLO <AWG/kcmil> — 2000V — EPR/XL-CPE — 90C WET/DRY — (UL) RHH/RHW-2 — CSA RW90 1000V FT4 -40C — FOR CT USE — SUN RES — P-07-KA140001-MSHA
Supply | Standard packing: 1,000 ft (305 m) or 2,500 ft (762 m) non-returnable wooden reels
Supply | Custom cut lengths: Project-cut lengths and factory-crimped tinned copper lugs available
Supply | Outer jacket colour: Black standard; red, blue, orange or grey to order
Supply | Export tariff code: HS 8544.49 (insulated electric conductors > 1,000 V)