## Request a quote
Request a quotation for DPNP / TPNP / FPNP
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/jis-flexible-shipboard-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
DPNP / TPNP / FPNP JIS Flexible Shipboard Rubber Cable – Dimensions, weight & 45 °C ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-flexible-shipboard-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 / IEC 60092-353 / ClassNK. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | JIS designation | Cores × cross-section | Outer Ø ≈ mm | Weight ≈ kg/km | Max. DC R Ω/km | Ampacity 45°C A | Series
| DPNP-2.5 | 2 × 2.5 mm² Flexible | 12.6 | 215 | 8.06 | 26 | JIS C 3410 0.6/1 kV Flexible EPR/Neoprene Shipboard Cables
| TPNP-2.5 | 3 × 2.5 mm² Flexible | 13.4 | 255 | 8.06 | 22 | JIS C 3410 0.6/1 kV Flexible EPR/Neoprene Shipboard Cables
| FPNP-4 | 4 × 4.0 mm² Flexible | 16.2 | 395 | 5.09 | 29 | JIS C 3410 0.6/1 kV Flexible EPR/Neoprene Shipboard Cables
| FPNP-10 | 4 × 10 mm² Flexible | 21.8 | 780 | 1.95 | 51 | JIS C 3410 0.6/1 kV Flexible EPR/Neoprene Shipboard Cables
| FPNP-25 | 4 × 25 mm² Flexible | 29.5 | 1560 | 0.79 | 89 | JIS C 3410 0.6/1 kV Flexible EPR/Neoprene Shipboard Cables
| FPNP-50 | 4 × 50 mm² Flexible | 38 | 2790 | 0.39 | 135 | JIS C 3410 0.6/1 kV Flexible EPR/Neoprene Shipboard Cables
In 4-core FPNP cables, the fourth (Green) core serves as the protective earthing conductor for portable metallic equipment.

## Technical data
DPNP / TPNP / FPNP JIS Flexible Shipboard Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-flexible-shipboard-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 / IEC 60092-353 / ClassNK. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standard | JIS C 3410 (Flexible shipboard cabtyre)
Key data | Voltage rating | 0.6/1 kV (3,500 V AC test voltage)
Key data | Configurations | 2C / 3C / 4C (DPNP (2), TPNP (3), FPNP (4))
Key data | Cross-sections | 1.5 to 95 mm² (Flexible Class 5 tinned Cu)
Key data | Insul. / Sheath | EPR / Neoprene ('P' EP-Rubber + 'NP' PCP)
Key data | Temperature | -30 to +90 °C (Weather-deck & engine room)
Electrical | Rated voltage (Uo/U) | 0.6 / 1 kV AC
Electrical | AC dielectric test | 3,500 V AC rms for 5 minutes
Electrical | Max. DC resistance @ 20 °C | 8.06 Ω/km (2.5) · 3.37 Ω/km (6) · 1.24 Ω/km (16) · 0.565 Ω/km (35)
Electrical | Insulation resistance | ≥ 400 to 600 MΩ·km @ 20 °C
Thermal | Max. conductor operating temp. | +90 °C continuous
Thermal | Flexing / fixed ambient temp. | -30 °C to +60 °C ambient
Thermal | Short-circuit temperature | +250 °C (5 s)
Mechanical | Min. bend radius | 6 × OD (free flexing & portable reeling) · 4 × OD (fixed)
Mechanical | Jacket tensile & elongation | ≥ 10.0 N/mm² tensile strength, ≥ 300 % elongation at break
Mechanical | Impact & crush resistance | Vulcanized cabtyre structure resists hatch and foot traffic
Resistance | Hot oil immersion test | 100 °C × 24 h mineral oil immersion per JIS C 3410
Resistance | Flame retardancy | IEC 60332-1-2 vertical flame self-extinguishing
Resistance | Weather & seawater resist. | Polychloroprene (NP) resists UV, ozone & continuous salt spray
Standards | Governing standard | JIS C 3410 (Flexible Cables for Electrical Appliances on Shipboard)
Standards | Class approvals | ClassNK, ABS, LR, DNV, BV, KR, CCS
Standards | RoHS & SOLAS | IMO SOLAS asbestos-free & RoHS 2 compliant
Identification | JIS code breakdown | D/T/F = 2/3/4 cores · P = EPR insulation · NP = Neoprene sheath
Identification | Core identification | 2C: Black, White · 3C: Black, White, Red · 4C: Black, White, Red, Green
Identification | Customs tariff (HS) | 8544.4993

## Construction
DPNP / TPNP / FPNP JIS Flexible Shipboard Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-flexible-shipboard-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 / IEC 60092-353 / ClassNK. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible Class 5 tinned annealed copper conductors | Fine-stranded tinned annealed copper per JIS C 3410 / IEC 60228 Class 5 (1.5 mm² to 95 mm²)
2 | Ethylene Propylene Rubber ('P') core insulation | 90 °C marine EP-rubber (EPR) thermoset insulation with colour/number core coding | Remains flexible from -30 °C to +90 °C
3 | Cabtyre elastomeric filler & rubberized cloth tape | Vulcanized rubber interstitial filler and proofed textile binder tape
4 | Polychloroprene ('NP' Neoprene) heavy-duty jacket | Cross-linked Polychloroprene (PCP / Neoprene) thermoset outer sheath (Black)
| DPNP (2-Core · 1.5 to 35 mm²) | 2-core flexible EPR/neoprene shipboard cable for single-phase deck lamps, heaters and DC tools
| TPNP (3-Core · 1.5 to 95 mm²) | 3-core flexible EPR/neoprene shipboard cable for 440 V 3-phase delta marine deck motors and pumps
| FPNP (4-Core · 1.5 to 95 mm²) | 4-core (3 phases + earth) flexible EPR/neoprene cable for portable welders, pumps and reefers

## Quality and supply
DPNP / TPNP / FPNP JIS Flexible Shipboard Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/jis-flexible-shipboard-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on JIS C 3410 / IEC 60092-353 / ClassNK. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3.5 kV AC dielectric, IR & conductor resistance test — Zero breakdown for 5 min and DC R within JIS C 3410 Class 5 limits | Every manufactured drum length
Sample test | Neoprene (NP) hot mineral oil immersion & tear test — Retains ≥ 60 % tensile/elongation after 100 °C × 24 h oil bath | Per production lot
Type test | Dynamic flexing & IEC 60332-1-2 flame propagation test — No strand breakage after flexing and self-extinguishing burn | Class society type approval
Standard / approval | JIS C 3410 Portable Marine
Standard / approval | ClassNK / ABS / LR / DNV
Standard / approval | IEC 60332-1-2 Flame Retardant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX JIS C 3410 DPNP / TPNP / FPNP 0.6/1kV
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP