## Request a quote
Request a quotation for DTS BSSA N
Application engineer · optical & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/brusens-dts-bssa-n-non-metallic-stainless-tube-temperature-sensing-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
DTS BSSA N Non-Metallic Stainless-Tube Temperature Sensing Cable – Dimensions & mechanical ratings (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/brusens-dts-bssa-n-non-metallic-stainless-tube-temperature-sensing-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 61757-2-2 / IEC 60794-1-21 / EN 54-22. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Fibre compliment & jacket | Outer Ø mm | Weight ≈ kg/km | Max. pull N | Crush N/100 mm | Series
| DTS BSSA N-02MM | 2 × 50/125 OM3 · LSZH | 3.8 | 22 | 1000 | 3000 | BSSA N — 316L FIMT + Aramid + Polymer Sheath
| DTS BSSA N-04MM | 4 × 50/125 OM3 · LSZH | 3.8 | 23 | 1000 | 3000 | BSSA N — 316L FIMT + Aramid + Polymer Sheath
| DTS BSSA N-02MM02SM | 2 × OM3 + 2 × G.652.D SM · PA12 | 3.8 | 21 | 1000 | 3000 | BSSA N — 316L FIMT + Aramid + Polymer Sheath
| DTS BSSA N-04MM02SM | 4 × OM3 + 2 × G.652.D SM · HDPE | 4.2 | 26 | 1200 | 3000 | BSSA N — 316L FIMT + Aramid + Polymer Sheath
Dry-FIMT version available for -196 °C LNG cryogenic tank leak monitoring where tube gel would freeze.

## Technical data
DTS BSSA N Non-Metallic Stainless-Tube Temperature Sensing Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/brusens-dts-bssa-n-non-metallic-stainless-tube-temperature-sensing-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 61757-2-2 / IEC 60794-1-21 / EN 54-22. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Sensing mode | Raman / BOTDA (Strain-free FIMT optical core)
Key data | Outer Ø | 3.8 to 4.2 mm (Compact fast-thermal-response)
Key data | Thermal τ₆₃ | ≤ 1.8 s in water (Direct 316L tube heat transfer)
Key data | Tensile load | 1,000 N max (316L FIMT + aramid yarns)
Key data | Crush rating | 3,000 N/100 mm (Stainless-steel tube shield)
Key data | Temperature | -40 to +85 °C (+150 °C short-term peak)
Electrical | Sensing principle | Raman OTDR (MM) & Brillouin BOTDA/BOTDR (SM)
Electrical | Temperature resolution | ±0.1 °C to ±0.5 °C (interrogator-dependent)
Electrical | Metallic cross-section | ≈ 0.9 mm² 316L stainless tube (single-point earthing)
Thermal | Operating temperature | -40 °C to +85 °C (-196 °C LNG cryo dry-tube option)
Thermal | Thermal response (τ₆₃) | ≤ 1.8 s in water · ≤ 6.5 s in air
Thermal | Short-term fire exposure | Up to +150 °C (sheath) / +400 °C (316L tube integrity)
Mechanical | Outer diameter | 3.8 mm (2–4F) · 4.2 mm (6F)
Mechanical | Max. tensile load | 1,000 N installation · 500 N permanent
Mechanical | Crush resistance | 3,000 N / 100 mm
Mechanical | Min. bend radius | 15 × OD static · 20 × OD dynamic
Optical | Multimode fibres | 50/125 µm OM3 (≤ 2.4 / 0.6 dB/km @ 850/1300 nm)
Optical | Single-mode fibres | ITU-T G.652.D / G.657.A1 (≤ 0.35 / 0.21 dB/km)
Optical | Excess fibre length | 0.20 % to 0.35 % strain-free inside 316L FIMT
Resistance | Hydrostatic pressure | 30 MPa (300 bar) on 316L FIMT
Resistance | Flame & smoke (LSZH) | IEC 60332-3-24, IEC 60754-2 & IEC 61034-2
Resistance | Chemical resistance | PA12 / HDPE resists hydrocarbons, acids & brine
Standards | DTS & LHD standards | IEC 61757-2-2 & EN 54-22
Standards | Cable test standard | IEC 60794-1-21 & IEC 60794-1-22
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Sheath colour | Red (Fire LHD), Orange (LSZH), or Black (PA/HDPE)
Identification | Fibre colour code | TIA-598-D 12-colour
Identification | Customs tariff (HS) | 8544.7000

## Construction
DTS BSSA N Non-Metallic Stainless-Tube Temperature Sensing Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/brusens-dts-bssa-n-non-metallic-stainless-tube-temperature-sensing-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 61757-2-2 / IEC 60794-1-21 / EN 54-22. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Strain-free DTS sensing fibres | 2 to 6 × 50/125 µm OM3 multimode and/or 9/125 µm G.652.D/G.657.A1 single-mode fibres with ≥ 0.2 % EFL
2 | Laser-welded 316L stainless-steel FIMT | Hermetically welded AISI 316L stainless-steel tube (Ø 1.8–2.2 mm, dry or gel-filled)
3 | Non-metallic aramid tensile layer | High-modulus polyaramid yarns stranded over the 316L FIMT (no outer steel wires)
4 | Fast-response outer sheath | Halogen-free flame-retardant LSZH (Red/Orange), Polyarnide 12 (PA12), or HDPE
| BSSA N-LSZH (Tunnel Fire LHD) | Red/Orange LSZH sheath (IEC 60332-3-24 / EN 54-22) for tunnel, tray and building fire detection
| BSSA N-PA / HDPE (Duct & Dam) | Black PA12 or HDPE sheath for microduct blowing alongside HV power cables and dam drains

## Quality and supply
DTS BSSA N Non-Metallic Stainless-Tube Temperature Sensing Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/brusens-dts-bssa-n-non-metallic-stainless-tube-temperature-sensing-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 61757-2-2 / IEC 60794-1-21 / EN 54-22. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % eddy-current FIMT weld & OTDR test — Hermetic 316L weld and ≤ 2.4/0.6 dB/km (MM) / ≤ 0.35/0.21 dB/km (SM) | Every drum length
Type test | EN 54-22 thermal response & fire classification — τ₆₃ ≤ 1.8 s in water and pass IEC 60332-3-24 flame test | Type qualification
Type test | Crush & 300 bar hydrostatic pressure test — 3,000 N/100 mm crush and 30 MPa pressure with Δα ≤ 0.05 dB | Type qualification
Standard / approval | IEC 61757-2-2 & EN 54-22
Standard / approval | IEC 60332-3-24 LSZH
Standard / approval | RoHS 2 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX DTS BSSA N 316L FIMT TEMPERATURE CABLE
Supply | Delivery form: Fumigated export wooden or steel drums
Supply | Standard drum lengths: 1000 m · 2000 m · 4000 m (or custom cut lengths)
Supply | MOQ: 500 m (standard) · 1000 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP