## Request a quote
Request a quotation for DeviceNet
Share your protocol/frequency, jacket material (PVC, PUR, LSZH, FEP), and installation motion for DeviceNet.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/devicenet-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
DeviceNet Cable – Dimensions & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/devicenet-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ODVA DeviceNet Volume I (Thick Trunk & Thin Drop). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Conductor size | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| DeviceNet Thick Trunk Fixed PVC (15/18 AWG) | 2×15 AWG + 2×18 AWG (Thick PVC) | 1.65 / 0.82 mm² | 12.2 | 82 | 185 | 73 | Standard DeviceNet configurations
| DeviceNet Thick Drag-Chain PUR (15/18 AWG) | 2×15 AWG + 2×18 AWG (Thick Chain PUR) | 1.65 / 0.82 mm² | 12.2 | 84 | 178 | 73 | Standard DeviceNet configurations
| DeviceNet Mid-Size Trunk (16/20 AWG) | 2×16 AWG + 2×20 AWG (Mid Trunk) | 1.31 / 0.52 mm² | 9.8 | 56 | 122 | 59 | Standard DeviceNet configurations
| DeviceNet Thin Drop Fixed PVC (22/24 AWG) | 2×22 AWG + 2×24 AWG (Thin PVC) | 0.34 / 0.22 mm² | 6.9 | 29 | 64 | 41 | Standard DeviceNet configurations
| DeviceNet Thin Drag-Chain PUR (22/24 AWG) | 2×22 AWG + 2×24 AWG (Thin Chain PUR) | 0.34 / 0.22 mm² | 6.9 | 30 | 62 | 41 | Standard DeviceNet configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per ODVA DeviceNet Volume I (Thick Trunk & Thin Drop).

## Impedance, capacitance & attenu
DeviceNet Cable – Impedance, capacitance & attenuation (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/devicenet-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ODVA DeviceNet Volume I (Thick Trunk & Thin Drop). Values for your order are confirmed in the quotation.
Configuration | Impedance Z0 | Max. DC R @ 20 °C Ω/km | Mutual C pF/m ≈ | VoP % | Attenuation @ 20 °C dB/100m | Dielectric test V
2×15 AWG + 2×18 AWG (Thick PVC) | 120 Ω | 45.2 | 39.4 | 75 | 0.42 @ 0.125 · 0.81 @ 0.5 · 1.31 @ 1 MHz | 2000
2×15 AWG + 2×18 AWG (Thick Chain PUR) | 120 Ω | 45.2 | 39.4 | 75 | 0.45 @ 0.125 · 0.85 @ 0.5 · 1.38 @ 1 MHz | 2000
2×16 AWG + 2×20 AWG (Mid Trunk) | 120 Ω | 72 | 39.4 | 75 | 0.60 @ 0.125 · 1.15 @ 0.5 · 1.75 @ 1 MHz | 2000
2×22 AWG + 2×24 AWG (Thin PVC) | 120 Ω | 183.6 | 39.4 | 75 | 0.95 @ 0.125 · 1.64 @ 0.5 · 2.29 @ 1 MHz | 1500
2×22 AWG + 2×24 AWG (Thin Chain PUR) | 120 Ω | 183.6 | 39.4 | 75 | 0.98 @ 0.125 · 1.70 @ 0.5 · 2.35 @ 1 MHz | 1500
Transmission values (characteristic impedance Z0, mutual capacitance, VoP, and attenuation) are measured at +20 °C per ODVA DeviceNet Volume I (Thick Trunk & Thin Drop).

## Technical data
DeviceNet Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/devicenet-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ODVA DeviceNet Volume I (Thick Trunk & Thin Drop). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Data impedance | 120 Ω ± 12 Ω (At 1 MHz (Blue CAN_L / White CAN_H))
Key data | Thick Trunk | 15 AWG + 18 AWG (Power 15 AWG (8 A) · Data 18 AWG ·)
Key data | Thin Drop | 22 AWG + 24 AWG (Power 22 AWG (3 A) · Data 24 AWG · 6.9)
Key data | Data capacitance | ≈ 39 pF / m (Foamed PE O2YS · VoP 75 %)
Key data | Data rates | 125 / 250 / 500k (Up to 500 m trunk on Thick cable)
Key data | UL approvals | CL2 / CMG / PLTC (300 V / 600 V tray & drag-chain)
Electrical | Data pair impedance Z0 | 120 Ω ± 12 Ω at 1 MHz (Blue / White)
Electrical | Data pair capacitance & VoP | ≈ 39.4 pF/m · VoP ≈ 75 % (delay ≤ 4.46 ns/m)
Electrical | Data pair attenuation (125 / 500 | Thick: 0.42 / 0.81 / 1.31 dB/100m · Thin
Electrical | Power pair DC resistance @ 20 °C | Thick (15 AWG): ≤ 11.8 Ω/km · Thin (22
Electrical | Data pair DC resistance @ 20 °C | Thick (18 AWG): ≤ 22.6 Ω/km · Thin (24
Electrical | Operating voltage & current | 300 V (CL2/CMG/PLTC) / 600 V AWM · 8 A
Thermal | Operating temp. (fixed / flex) | -40 °C to +80 °C fixed · -30 °C to +75 °C
Thermal | Storage temperature | -40 °C to +80 °C
Mechanical | Outer diameter (Thick / Thin) | 12.2 mm ± 0.3 mm (Thick) · 6.9 mm ± 0.2 mm
Mechanical | Min. bending radius | 6 × D fixed · 10 × D drag-chain
Resistance | Oil & coolant resistance | UL Oil Res I/II · EN 60811-404
Resistance | Flame retardancy | UL 1685 FT4 / CMG / PLTC · IEC 60332-1-2
Standards | Primary specification | ODVA DeviceNet Specification Volume I
Standards | North American listings | UL CL2 / CL3 / CMG / PLTC · CSA CMG FT4
Identification | Core colours (ODVA mandatory) | Data: Blue (CAN_L), White (CAN_H) · Power
Identification | Outer sheath colour | RAL 7001 Grey (standard), RAL 4001 Violet

## Construction
DeviceNet Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/devicenet-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ODVA DeviceNet Volume I (Thick Trunk & Thin Drop). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned copper data & power | Thick: 2×18 AWG data + 2×15 AWG power + 18 AWG drain · Thin: 2×24 AWG data + 2×22 AWG
2 | Foamed PE (data) & PVC/PE (power) | Low-loss foamed PE on Blue/White 120 Ω data pair; SR-PVC or PE on Red/Black 24 V power
3 | Individual Al/PET pair screens | 100 % coverage aluminium/polyester foil tape applied separately over the data pair and
4 | Overall tinned copper braid + drain | Tinned copper wire braid (≥65–85 % coverage) in contact with central stranded tinned Cu
5 | Industrial outer sheath | Sunlight- and oil-resistant Grey, Violet, or Yellow PVC (CL2/CMG/PLTC), TPE, or | UL 13 PLTC / UL 444 CMG
| DeviceNet Thick Trunk (15 AWG Power + 18 AWG Data, OD 12.2 mm) | Main backbone trunk cable for 500 m reach and 8 A 24 V DC power (Fixed PVC/CPE or Drag-Chain PUR).
| DeviceNet Thin Drop (22 AWG Power + 24 AWG Data, OD 6.9 mm) | Flexible drop and short-trunk cable for 6 m drops / 100 m trunks and 3 A power (Fixed PVC or Drag-Chain PUR).

## Quality and supply
DeviceNet Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/devicenet-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ODVA DeviceNet Volume I (Thick Trunk & Thin Drop). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1 MHz data-pair Z0, capacitance & attenuation — Z0 = 120 ± 12 Ω; attenuation ≤ 1.31 (Thick) / ≤ 2.29 (Thin) dB/100m @ 1 MHz | 100 % of reels
Routine test | Power & data DC resistance + 2 kV dielectric — ODVA Volume I resistance limits; 1.5–2.0 kV dielectric | 100 % of reels
Sample test | Data-to-power pair crosstalk isolation — Individual Al/PET screens prevent 24 V switching noise coupling | Per production batch
Type test | UL CMG/PLTC FT4 tray flame & drag-chain flex — Pass UL 1685 FT4 & ≥ 5M cycles on PUR variants | Type approval
Standard / approval | ODVA Volume I
Standard / approval | UL CL2 / CMG / PLTC
Standard / approval | CSA CMG FT4 / CE
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX ODVA DEVICENET THICK / THIN 120
Supply | Delivery form: Non-returnable plywood reels or export drums
Supply | Standard reel lengths: 100 m · 305 m · 500 m · 1000 m
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP