## Request a quote
Request a quotation for Dynamic Inter-Array Cable
Dynamic submarine cable engineer
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/floating-offshore-wind-dynamic-medium-voltage-inter-array-subsea-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Dynamic Inter-Array Cable – Dimensions, weights & pulling loads (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/floating-offshore-wind-dynamic-medium-voltage-inter-array-subsea-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 63026 / CIGRE TB 610 / CIGRE TB 722. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² + Optical | Voltage kV | Nominal OD mm | Copper kg/km | Weight in air kg/km | Weight in sea kg/km | Max pull kN | Dynamic MBR mm | Series
| DIAC-33-3X95-48FO | 3 × 95 mm² + 2×24FO | 18/30 | 112 | 3180 | 21400 | 11300 | 150 | 2240 | 33 kV (18/30(36) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-33-3X150-48FO | 3 × 150 mm² + 2×24FO | 18/30 | 121.5 | 4760 | 25800 | 13900 | 185 | 2430 | 33 kV (18/30(36) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-33-3X240-48FO | 3 × 240 mm² + 2×24FO | 18/30 | 134 | 7350 | 32900 | 18400 | 230 | 2680 | 33 kV (18/30(36) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-33-3X300-48FO | 3 × 300 mm² + 2×24FO | 18/30 | 141.5 | 9080 | 37600 | 21400 | 260 | 2830 | 33 kV (18/30(36) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-33-3X400-48FO | 3 × 400 mm² + 2×24FO | 18/30 | 151 | 11960 | 44500 | 26100 | 300 | 3020 | 33 kV (18/30(36) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-33-3X500-48FO | 3 × 500 mm² + 2×24FO | 18/30 | 160.5 | 14840 | 51800 | 31000 | 340 | 3210 | 33 kV (18/30(36) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-33-3X630-48FO | 3 × 630 mm² + 2×24FO | 18/30 | 171 | 18580 | 60900 | 37400 | 390 | 3420 | 33 kV (18/30(36) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-66-3X150-48FO | 3 × 150 mm² + 2×24FO | 36/66 | 142 | 4920 | 31800 | 15600 | 210 | 2840 | 66 kV (36/66(72.5) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-66-3X240-48FO | 3 × 240 mm² + 2×24FO | 36/66 | 154.5 | 7520 | 39400 | 20200 | 255 | 3090 | 66 kV (36/66(72.5) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-66-3X300-48FO | 3 × 300 mm² + 2×24FO | 36/66 | 162 | 9260 | 44600 | 23500 | 285 | 3240 | 66 kV (36/66(72.5) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-66-3X400-48FO | 3 × 400 mm² + 2×24FO | 36/66 | 172.5 | 12150 | 52400 | 28600 | 330 | 3450 | 66 kV (36/66(72.5) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-66-3X500-48FO | 3 × 500 mm² + 2×24FO | 36/66 | 182 | 15040 | 60200 | 33800 | 370 | 3640 | 66 kV (36/66(72.5) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-66-3X630-48FO | 3 × 630 mm² + 2×24FO | 36/66 | 193.5 | 18800 | 70100 | 40500 | 415 | 3870 | 66 kV (36/66(72.5) kV) Dynamic Three-Core Inter-Array Cables
| DIAC-66-3X800-48FO | 3 × 800 mm² + 2×24FO | 36/66 | 206 | 23680 | 82400 | 48900 | 460 | 4120 | 66 kV (36/66(72.5) kV) Dynamic Three-Core Inter-Array Cables
Max pull (kN) represents the allowable installation and extreme storm axial tension with contra-helical steel wire armour per CIGRE TB 610.

## Technical data
Dynamic Inter-Array Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/floating-offshore-wind-dynamic-medium-voltage-inter-array-subsea-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 63026 / CIGRE TB 610 / CIGRE TB 722. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage grade | 33 kV / 66 kV (18/30(36) & 36/66(72.5) kV AC)
Key data | Conductor | 3 × 95–800 mm² (Water-blocked compacted copper)
Key data | Radial barrier | Cu / CuNi Screen (Fatigue-resistant corrugated sheath)
Key data | Optical unit | 24–48 SM Fibres (Dual interstitial 316L FIMT tubes)
Key data | Design life | 25–30 Years (10⁷ wave-cycle fatigue qualified)
Key data | Standard | IEC 63026 (CIGRE TB 610 / TB 722 & DNV-RP-F401)
Electrical | Rated voltage U0/U (Um) | 18/30 (36) kV & 36/66 (72.5) kV AC
Electrical | AC routine test voltage | 45 kV AC (33 kV) / 90 kV AC (66 kV) for 30 min
Electrical | Partial discharge at 2 × U0 | ≤ 5 pC (no detectable discharge)
Electrical | Impulse withstand (BIL) | 170 kVp (33 kV) · 325 kVp (66 kV)
Electrical | Current rating (3 cores) | 285 A (95 mm²) to 920 A (800 mm²) in seawater
Thermal | Max. conductor temperature | +90 °C continuous
Thermal | Short-circuit temperature | +250 °C (up to 5 s)
Thermal | Seawater & seabed ambient | −5 °C to +35 °C
Mechanical | Design water depth | 50 m to 1,000 m (lazy-wave / tethered-wave)
Mechanical | Fatigue life qualification | ≥ 10⁷ bending cycles (25–30 year metocean spectrum)
Mechanical | Min. bend radius (dynamic) | 20 × OD (guided by bend stiffener)
Mechanical | Min. bend radius (static) | 12 × OD (seabed & carousel storage)
Mechanical | Max. installation tension | 120 kN to 450 kN (per CIGRE TB 610)
Optical | Fibre type & count | 2 × 24 or 2 × 48 ITU-T G.652.D SM + MM DTS fibres
Optical | Attenuation (1310 / 1550 nm) | ≤ 0.35 dB/km / ≤ 0.21 dB/km
Resistance | Radial water barrier | Corrugated welded Cu/CuNi sheath (100 % impervious)
Resistance | Longitudinal water block | Swellable conductor & screen tapes (IEC 60840 Annex G)
Resistance | Marine growth & abrasion | Extruded HDPE outer jacket for clamp/stiffener zones
Standards | Primary FOWT cable standard | IEC 63026
Standards | Mechanical & fatigue testing | CIGRE TB 610 / TB 722 / TB 862
Standards | Subsea power design rules | DNV-RP-F401 / DNV-ST-0359
Identification | Outer sheath | Black extruded HDPE with co-extruded yellow longitudinal stripes
Identification | Phase core identification | Numbered/colour-coded phases 1, 2, 3
Identification | Customs tariff (HS) | 8544.60

## Construction
Dynamic Inter-Array Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/floating-offshore-wind-dynamic-medium-voltage-inter-array-subsea-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 63026 / CIGRE TB 610 / CIGRE TB 722. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Longitudinally water-blocked conductor | Compacted circular stranded copper (IEC 60228 Class 2 or flexible Class 5) with water-swellable yarns/compound
2 | Triple-extruded WTR-XLPE / EPR system | Extruded conductor screen, water-tree-retardant XLPE or EPR insulation (18/30 kV or 36/66 kV), and bonded insulation screen
3 | Fatigue-resistant radial water barrier | Formed and laser-welded corrugated copper or copper-nickel sheath (or heavy copper wire screen on wet-design EPR)
4 | Dual interstitial 316L FIMT optical units | Two laser-welded stainless-steel FIMT tubes (24 or 48 ITU-T G.652.D fibres each) for SCADA and DTS/DAS fatigue monitoring
5 | Contra-helical dynamic wire armour | Two opposing-lay layers of galvanised high-tensile steel armour wires embedded in bitumen-free polymeric bedding
6 | Extruded HDPE outer serving | Abrasion-resistant high-density polyethylene (HDPE) outer jacket with yellow warning stripes (replaces polypropylene yarn at bend stiffener)
| DIAC-33 (18/30(36) kV Dynamic Array) | 33 kV three-core dynamic submarine cable (95–630 mm²) with wet-aged WTR-XLPE/EPR or corrugated copper screen
| DIAC-66 (36/66(72.5) kV Dynamic Array) | 66 kV high-capacity three-core dynamic inter-array cable (150–800 mm²) for 12–20 MW floating wind turbines

## Quality and supply
Dynamic Inter-Array Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/floating-offshore-wind-dynamic-medium-voltage-inter-array-subsea-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 63026 / CIGRE TB 610 / CIGRE TB 722. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | HV AC withstand & partial discharge test — 2.5 × U0 (45 kV / 90 kV AC) for 30 min + PD ≤ 5 pC at 2 × U0 | Every manufactured cable length
Sample test | Conductor & screen longitudinal water penetration test — Zero leakage under hydrostatic head per IEC 63026 / IEC 60840 | Sample per production batch
Type test | Full-scale dynamic mechanical fatigue + electrical type test — CIGRE TB 610 / IEC 63026 combined tension-bending fatigue followed by 20 thermal cycles & BIL impulse test | Type qualification
Type test | Corrugated metallic sheath S-N fatigue curve verification — Validate strain endurance beyond 10⁷ metocean wave cycles | Type approval
Standard / approval | IEC 63026 Floating Offshore Wind Qualification
Standard / approval | CIGRE TB 610 / TB 722 & DNV-RP-F401 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX DIAC 33/66kV DYNAMIC INTER-ARRAY SUBSEA CABLE IEC 63026 [SIZE] [YEAR]
Supply | Delivery form: Direct turntable load-out to cable-lay vessel or heavy transport reels
Supply | Dynamic accessories: Engineered bend stiffeners, I-tube hang-off clamps, buoyancy modules &タッチdown protection
Supply | Monitoring fibres: Pre-terminated DTS/DAS & SCADA optical breakout box
Supply | Lead time: Project-scheduled manufacture