## Request a quote
Request a quotation for EGPF
Application engineer · process instrumentation & Ex-i/Ex-d
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/nf-m-87-202-egpf-lead-sheathed-armoured-instrument-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
NF M 87-202 EGPF Lead-Sheathed & Steel-Tape Armoured Hydrocarbon – Dimensions, construction & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nf-m-87-202-egpf-lead-sheathed-armoured-instrument-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on NF M 87-202 / IEC 60332-3. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Outer Ø ≈ mm | Weight ≈ kg/km | Min. bend R fixed mm | Series
| EGPF 1×2×0.5 | 1×2×0.5 mm² | 6.4 | 58 | 52 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 2×2×0.5 | 2×2×0.5 mm² | 9.2 | 112 | 74 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 4×2×0.5 | 4×2×0.5 mm² | 11.4 | 176 | 92 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 8×2×0.5 | 8×2×0.5 mm² | 14.8 | 295 | 118 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 12×2×0.5 | 12×2×0.5 mm² | 17.6 | 420 | 141 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 1×2×1.0 | 1×2×1.0 mm² | 7.6 | 86 | 61 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 2×2×1.0 | 2×2×1.0 mm² | 11 | 168 | 88 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 4×2×1.0 | 4×2×1.0 mm² | 13.5 | 264 | 108 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 8×2×1.0 | 8×2×1.0 mm² | 17.9 | 465 | 143 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 1×2×1.5 | 1×2×1.5 mm² | 8.5 | 114 | 68 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 4×2×1.5 | 4×2×1.5 mm² | 15.2 | 348 | 122 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
| EGPF 12×2×1.5 | 12×2×1.5 mm² | 23.4 | 860 | 187 | EGPF Standard Construction Schedule (500 V · −30…+70 °C)
Additional pair/triad/quad counts (up to 48 pairs) and blue Ex-i intrinsically safe outer sheaths available per NF M 87-202 / IEC 60332-3.

## Electrical parameters by conduc
NF M 87-202 EGPF Lead-Sheathed & Steel-Tape Armoured Hydrocarbon – Electrical parameters by conductor cross-section (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/nf-m-87-202-egpf-lead-sheathed-armoured-instrument-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on NF M 87-202 / IEC 60332-3. Values for your order are confirmed in the quotation.
Conductor size | Max. DC R₂₀ Ω/km | Mutual cap. ≈ nF/km | Inductance ≈ mH/km
0.50 mm² (7/0.30 mm · AWG 20) | 39 | 115 | 0.65
0.75 mm² (7/0.37 mm · AWG 18) | 26 | 120 | 0.62
1.00 mm² (7/0.43 mm · AWG 17) | 19.5 | 125 | 0.6
1.50 mm² (7/0.53 mm · AWG 16) | 13.3 | 135 | 0.58
2.50 mm² (7/0.67 mm · AWG 14) | 7.98 | 145 | 0.55
L/R ratio ≤ 25 µH/Ω (0.5–1.0 mm²) and ≤ 40 µH/Ω (1.5 mm²) for intrinsically safe Ex-i circuits.

## Technical data
NF M 87-202 EGPF Lead-Sheathed & Steel-Tape Armoured Hydrocarbon – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/nf-m-87-202-egpf-lead-sheathed-armoured-instrument-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on NF M 87-202 / IEC 60332-3. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 500 V (Per NF M 87-202 / IEC 60332-3)
Key data | Operating temp. | −30…+70 °C (Continuous thermal rating)
Key data | Min. bend radius | 12 × OD (Installed / fixed routing)
Key data | Conductor | stranded copper (High-conductivity stranded copper)
Key data | Outer layer | PVC outer sheath (Extruded PVC outer sheath protective)
Key data | Standard | NF M 87-202 (NF M 87-202 / IEC 60332-3)
Electrical | Rated voltage / duty | 500 V (NF M 87-202 / IEC 60332-3)
Electrical | Conductor construction | Stranded stranded copper conductor — High-conductivity stranded copper conductor per NF M 87-202 / IEC 60332-3
Electrical | Primary insulation / dielectric | PVC core insulation — Extruded PVC dielectric (individual core / group layer)
Thermal | Continuous operating temperature | −30…+70 °C per NF M 87-202 / IEC 60332-3
Thermal | Short-circuit / peak thermal limit | +160 °C to +250 °C (5 s adiabatic limit depending on dielectric class)
Thermal | Minimum installation temperature | −5 °C (thermoplastic) / −25 °C (cross-linked or elastomer) / −40 °C (metallic)
Mechanical | Outer protection / covering | PVC outer sheath — Extruded PVC outer sheath protective layer (continuous layer)
Mechanical | Minimum bending radius | 12 × OD (installed / static routing)
Mechanical | Layer count & geometry | 9 concentric/structural layers verified by cross-section inspection
Resistance | Environmental & chemical durability | Engineered for industrial service in accordance with NF M 87-202 / IEC 60332-3
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing product standard | NF M 87-202 / IEC 60332-3
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | EGPF
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 7614.10

## Construction
NF M 87-202 EGPF Lead-Sheathed & Steel-Tape Armoured Hydrocarbon – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/nf-m-87-202-egpf-lead-sheathed-armoured-instrument-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on NF M 87-202 / IEC 60332-3. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded stranded copper conductor | High-conductivity stranded copper conductor per NF M 87-202 / IEC 60332-3 | NF M 87-202 / IEC 60332-3
2 | PVC core insulation | Extruded PVC dielectric (individual core / group layer) | NF M 87-202 / IEC 60332-3
3 | Plastic binder tape | Helically applied plastic binder tape | NF M 87-202 / IEC 60332-3
4 | Al/PET overall screen | Al/PET overall screen metallic electromagnetic screen (lapped tape) | NF M 87-202 / IEC 60332-3
5 | PVC inner sheath | Extruded PVC inner sheath protective layer (continuous layer) | NF M 87-202 / IEC 60332-3
6 | Lead moisture barrier | Extruded Lead moisture barrier protective layer (continuous layer) | NF M 87-202 / IEC 60332-3
7 | Inner steel armour tape | Inner steel armour tape mechanical protection (lapped tape) | NF M 87-202 / IEC 60332-3
8 | Outer steel armour tape | Outer steel armour tape mechanical protection (lapped tape) | NF M 87-202 / IEC 60332-3
9 | PVC outer sheath | Extruded PVC outer sheath protective layer (continuous layer) | NF M 87-202 / IEC 60332-3
| EGPF — Standard Execution | Built to NF M 87-202 / IEC 60332-3 with stranded stranded copper conductor and pvc outer sheath
| EGPF — Custom Cross-Sections | Full range of metric mm² and AWG/kcmil conductor sizes per NF M 87-202 / IEC 60332-3
| EGPF — Export Drum Supply | Supplied with EN 10204 3.1 routine dielectric & conductor resistance test certificate

## Quality and supply
NF M 87-202 EGPF Lead-Sheathed & Steel-Tape Armoured Hydrocarbon – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/nf-m-87-202-egpf-lead-sheathed-armoured-instrument-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on NF M 87-202 / IEC 60332-3. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (NF M 87-202 / IEC 60332-3) — DC resistance at 20 °C and geometry within NF M 87-202 / IEC 60332-3 class limits | Every manufactured drum / spool
Routine test | Routine dielectric / spark / structural integrity test (NF M 87-202 / IEC 60332-3) — Zero breakdown or structural defect over full production length | Every manufactured drum / spool
Type test | Thermal aging, mechanical & material qualification (NF M 87-202 / IEC 60332-3) — Full compliance with NF M 87-202 / IEC 60332-3 across −30…+70 °C | Type qualification & periodic sample audit
Standard / approval | NF M 87-202 Compliant
Standard / approval | EN 10204 3.1 Routine Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX EGPF <size> NF M 87-202 500 V CE
Supply | Delivery form: Non-returnable fumigated wooden drums or precision DIN spools
Supply | Standard lengths: 500 m · 1000 m · 2000 m drums (custom cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP