## Request a quote
Request a quotation for EN 50382-2
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/high-temperature-rolling-stock-power-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
EN 50382-2 High-Temperature Rolling Stock Power Cable – Dimensions & masses (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/high-temperature-rolling-stock-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 50382-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Size / Configuration | Stranding · Wall | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| EN 50382-2 1×10 (1.8/3 kV) | 1×10 (1.8/3 kV) | 0.21 · 2.3 mm | 9.6 | 84.1 | 145 | 57.6 | EN 50382-2 size schedule
| EN 50382-2 1×25 (1.8/3 kV) | 1×25 (1.8/3 kV) | 0.21 · 2.3 mm | 11.8 | 171.1 | 295 | 70.8 | EN 50382-2 size schedule
| EN 50382-2 1×50 (1.8/3 kV) | 1×50 (1.8/3 kV) | 0.31 · 2.3 mm | 14.5 | 310.3 | 535 | 87 | EN 50382-2 size schedule
| EN 50382-2 1×70 (1.8/3 kV) | 1×70 (1.8/3 kV) | 0.31 · 2.3 mm | 16.4 | 420.5 | 725 | 98.4 | EN 50382-2 size schedule
| EN 50382-2 1×95 (1.8/3 kV) | 1×95 (1.8/3 kV) | 0.31 · 2.5 mm | 18.8 | 559.7 | 965 | 112.8 | EN 50382-2 size schedule
| EN 50382-2 1×120 (1.8/3 kV) | 1×120 (1.8/3 kV) | 0.31 · 2.5 mm | 20.5 | 693.1 | 1195 | 123 | EN 50382-2 size schedule
| EN 50382-2 1×185 (1.8/3 kV) | 1×185 (1.8/3 kV) | 0.41 · 2.6 mm | 24.2 | 1049.8 | 1810 | 145.2 | EN 50382-2 size schedule
| EN 50382-2 1×240 (1.8/3 kV) | 1×240 (1.8/3 kV) | 0.41 · 2.8 mm | 27.3 | 1363 | 2350 | 163.8 | EN 50382-2 size schedule
Dimensions and tolerances conform to BS EN 50382-2.

## Electrical data
EN 50382-2 High-Temperature Rolling Stock Power Cable – Electrical data (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/high-temperature-rolling-stock-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 50382-2. Values for your order are confirmed in the quotation.
Size / Configuration | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
1×10 (1.8/3 kV) | 1.95 | 115 | 92
1×25 (1.8/3 kV) | 0.795 | 205 | 164
1×50 (1.8/3 kV) | 0.393 | 325 | 260
1×70 (1.8/3 kV) | 0.277 | 405 | 324
1×95 (1.8/3 kV) | 0.21 | 495 | 396
1×120 (1.8/3 kV) | 0.164 | 580 | 464
1×185 (1.8/3 kV) | 0.108 | 760 | 608
1×240 (1.8/3 kV) | 0.082 | 910 | 728
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
EN 50382-2 High-Temperature Rolling Stock Power Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/high-temperature-rolling-stock-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 50382-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.8/3 kV & 3.6/6 (Max 3.6 kV / 7.2 kV AC (5.4 kV / 9 kV DC)
Key data | Test voltage | 6500 V AC (1.8/3 (Dielectric withstand)
Key data | Operating temp | -50 to +150 °C (Short-circuit +300 °C)
Key data | Min. bend radius | 4 × D (Flexing 6 × D)
Key data | Primary standard | BS EN 50382-2 (BS EN 50382-2; BS EN 50382-1; EN 45545-2)
Key data | Flame rating | EN 45545-2 R15/R (Fire & safety compliance)
Electrical | Rated voltage (U0/U) | 1.8/3 kV & 3.6/6 kV AC
Electrical | Max. operating voltage | 3.6 kV / 7.2 kV AC (5.4 kV / 9 kV DC)
Electrical | Dielectric test voltage | 6500 V AC (1.8/3 kV) / 11000 V AC (3.6/6 kV)
Electrical | Insulation resistance | ≥ 500 MΩ·km at +20 °C
Thermal | Operating temperature range | -50 °C to +150 °C
Thermal | Dynamic / flexing temperature | -40 °C to +150 °C
Thermal | Max. short-circuit temperature | +300 °C
Mechanical | Min. bend radius (fixed) | 4 × D
Mechanical | Min. bend radius (flexing) | 6 × D
Mechanical | Max. tensile pulling load | 15 N/mm²
Mechanical | Vibration & mechanical duty | Bogie-to-carbody dynamic movement
Resistance | Flame retardancy | EN 45545-2 R15/R16 Hazard Level HL3; IEC 60332-1-2; IEC 60332-3-24; IEC 61034-2; IEC 60754-1/2
Resistance | Oil & fluid resistance | EN 50382-1 mineral oil, transformer fluid, acid & alkali resistant
Resistance | UV, weather & ozone | UV, ozone & extreme sub-zero (-50 °C) cold-impact resistant
Resistance | Chemical & environmental | Zero halogen, ultra-low smoke density, non-corrosive combustion gases (EN 60754-2)
Standards | Governing standard | BS EN 50382-2 (2008) — Railway applications — Cabling of rolling stock having special fire performance — High temperature power cables — Part 2: Single core silicone rubber insulated cables
Standards | Applicable clauses | BS EN 50382-2; BS EN 50382-1; EN 45545-2 HL1/HL2/HL3
Standards | Secondary reference | EN 45545-2 — Railway applications — Fire protection on railway vehicles — Requirement sets R15/R16 (HL3)
Identification | Core identification | Single-core high-temperature power conductor
Identification | Outer sheath colour | Black
Identification | Surface print legend | TEBAOFLEX — EN 50382-2 — 1.8/3 kV (or 3.6/6 kV) — 150°C — 1×<size> mm² — EN 45545-2 HL3

## Construction
EN 50382-2 High-Temperature Rolling Stock Power Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/high-temperature-rolling-stock-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 50382-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Conductor | Class 5 / Class 6 flexible tinned copper conductor (IEC 60228) | BS EN 50382-2
2 | Tape | Non-hygroscopic separator tape | BS EN 50382-2
3 | Insulation | High-temperature silicone rubber dielectric (EI 111 / EI 112, +150 °C) | BS EN 50382-2
4 | Sheath | LSZH flame-retardant silicone elastomer outer sheath (EM 107, Black) | BS EN 50382-2
| Bogie Traction Motor Jumper Leads | Class 6 extra-flexible tinned copper stranding and -50 °C to +150 °C silicone elastomer withstand continuous bogie articulation and winter track ballast impact.
| Traction Converter & Roof Braking Resistor Wiring | +150 °C continuous rating (short-circuit to +300 °C) allows smaller conductor cross-sections in thermally dense converter cabinets.
| Underground Metro & Tunnel Passenger Trains | Certified to EN 45545-2 Hazard Level HL3 (R15/R16) for zero halogen, minimal smoke, and flame containment in underground rail tunnels.

## Quality and supply
EN 50382-2 High-Temperature Rolling Stock Power Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/high-temperature-rolling-stock-power-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS EN 50382-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Dielectric voltage withstand & conductor DC resistance — 6500 V AC (1.8/3 kV) / 11000 V AC (3.6/6 kV) | 100 % of production lengths
Sample test | Insulation wall thickness, hot-set / pinch & cold bend — Conforms to BS EN 50382-2 sample schedule | Every production batch
Type test | Fluid immersion, flame propagation & thermal aging — EN 45545-2 R15/R16 Hazard Level HL3; IEC 60332-1-2; IEC 60332-3-24; IEC 61034-2; IEC 60754-1/2 | Type qualification
Standard / approval | BS EN 50382-2; BS EN 50382-1; EN 45545-2 HL1/HL2/HL3
Standard / approval | EN 45545-2 (2020)
Standard / approval | RoHS 3 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX — EN 50382-2 — 1.8/3 kV (or 3.6/6 kV) — 150°C — 1×<size> mm² — EN 45545-2 HL3
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP