## Request a quote
Request a quotation for ES3-FO & HVSC 6.6/11 KV
Share system voltage (6.6 kV or 11 kV), phase cross-section, pilot/optical fibre count, reel drum geometry and continuous cable length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/es3-fo-hvsc-6-6-11-kv/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
ES3-FO & HVSC 6.6/11 kV IEC/IEEE 80005-1 Extruded-Screen Cold-Ironing – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/es3-fo-hvsc-6-6-11-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| ES3-FO 3×70+2G25+24F | 3×70 + 2×25 mm² + 2×Pilot + 24F | IEC 60228 Class 5 flexible Cu/SnCu | 58 | 5420 | 31.5 | 580 | ES3-FO & HVSC 6.6/11 KV Construction Schedule (−40…+90 °C)
| ES3-FO 3×95+2G35+24F | 3×95 + 2×35 mm² + 2×Pilot + 24F | IEC 60228 Class 5 flexible Cu/SnCu | 63.5 | 6780 | 42.8 | 635 | ES3-FO & HVSC 6.6/11 KV Construction Schedule (−40…+90 °C)
| ES3-FO 3×150+2G50+24F | 3×150 + 2×50 mm² + 2×Pilot + 24F | IEC 60228 Class 5 flexible Cu/SnCu | 72.4 | 9350 | 67.5 | 725 | ES3-FO & HVSC 6.6/11 KV Construction Schedule (−40…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable.

## Electrical, optical & thermal p
ES3-FO & HVSC 6.6/11 kV IEC/IEEE 80005-1 Extruded-Screen Cold-Ironing – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/es3-fo-hvsc-6-6-11-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3×70 + 2×25 mm² + 2×Pilot + 24F | 0.272 | 6.6/11 kV (245 A HVSC) | −40…+90 °C
3×95 + 2×35 mm² + 2×Pilot + 24F | 0.193 | 6.6/11 kV (300 A HVSC) | −40…+90 °C
3×150 + 2×50 mm² + 2×Pilot + 24F | 0.124 | 6.6/11 kV (385 A HVSC) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
ES3-FO & HVSC 6.6/11 kV IEC/IEEE 80005-1 Extruded-Screen Cold-Ironing – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/es3-fo-hvsc-6-6-11-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 6.6/11 kV (Tested per IEC/IEEE 80005-1)
Key data | Operating temp. | −40…+90 °C (Continuous shipboard & offshore service)
Key data | Min. bend radius | 10 × OD (Marine tray, bulkhead & deck routing)
Key data | Core / conductor | ES3 Reduced-Wall (Flexible tinned copper + triple-extruded)
Key data | Outer protection | Shore Power Eco- (High-visibility green abrasion-, oil- an)
Key data | Standard | IEC/IEEE 80005-1 (IEC/IEEE 80005-1 Shore-to-Ship Cold-Iron)
Electrical | Rated voltage / transmission duty | 6.6/11 kV (IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable)
Electrical | Core / conductor construction | ES3 Reduced-Wall MV Phase Cores — Flexible tinned copper + triple-extruded ES3 HEPR + copper screen
Electrical | Primary dielectric / buffering | Earth Core + Pilot Pair + Optical Unit — Interstitial earth, pilot interlock pair and 12-fiber optical sub-unit
Thermal | Continuous operating temperature | −40…+90 °C (shipboard & offshore duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Shore Power Eco-Friendly Outer Jacket — High-visibility green abrasion-, oil- and seawater-resistant outer sheath
Mechanical | Minimum bending radius | 10 × OD
Mechanical | Armour, screen & mechanical duty | Anti-Torsion Braid & Inner Sheath — Double-sheathed reeling construction with anti-torsion textile braid
Resistance | Flame, fire & smoke performance | Qualified for marine flame-retardance and low-smoke zero-halogen / fire safety per IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable
Resistance | Oil, drilling mud & seawater resistance | Resistant to marine fuel/lube oils, salt mist and offshore fluids per IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable
Standards | Environmental & test standards | IEC 60228 / IEC 60332-3-22 / IEC 60754 / IEC 61034 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | ES3-FO & HVSC 6.6/11 KV
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Shore Power Eco-)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
ES3-FO & HVSC 6.6/11 kV IEC/IEEE 80005-1 Extruded-Screen Cold-Ironing – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/es3-fo-hvsc-6-6-11-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | ES3 Reduced-Wall MV Phase Cores | Flexible tinned copper + triple-extruded ES3 HEPR + copper screen
2 | Earth Core + Pilot Pair + Optical Unit | Interstitial earth, pilot interlock pair and 12-fiber optical sub-unit
3 | Anti-Torsion Braid & Inner Sheath | Double-sheathed reeling construction with anti-torsion textile braid
4 | Shore Power Eco-Friendly Outer Jacket | High-visibility green abrasion-, oil- and seawater-resistant outer sheath
| ES3-FO & HVSC 6.6/11 KV — Standard Shipboard & Offshore Execution | Built to IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable with es3 reduced-wall mv phase cores and shore power eco-friendly outer jacket
| ES3-FO & HVSC 6.6/11 KV — Custom Drum Length & Gland Kit | Available in custom continuous shipboard/offshore drum lengths or with marine EMC cable glands
| ES3-FO & HVSC 6.6/11 KV — Class & Routine Test Certified | Supplied with EN 10204 3.1 routine dielectric, conductor resistance & flame/fire test report

## Quality and supply
ES3-FO & HVSC 6.6/11 kV IEC/IEEE 80005-1 Extruded-Screen Cold-Ironing – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/es3-fo-hvsc-6-6-11-kv/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable) — DC resistance at 20 °C / optical attenuation and outer diameter within IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable) — Zero dielectric breakdown and verified insulation resistance for 6.6/11 kV rating | Every manufactured drum length
Type test | Flame, fire integrity, oil/mud & mechanical qualification (IEC/IEEE 80005-1 Shore-to-Ship Cold-Ironing (AMP) HVSC Reeling Cable) — Verified flame/fire performance, fluid resistance and thermal stability across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | IEC/IEEE 80005-1 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX ES3-FO & HVSC 6.6/11 KV IEC/IEEE 80005-1 6.6/11 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel marine reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous shipboard/offshore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP