## Request a quote
Request a quotation for EV / EVJ
Application engineer · EV charging & mobility cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ul-type-ev-evj-thermoplastic-electric-vehicle-charging-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
EV / EVJ UL Type EV / EVJ Thermoplastic Electric Vehicle Charging – Configuration, outer diameter & NEC 625 ampacity (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-type-ev-evj-thermoplastic-electric-vehicle-charging-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Article 625 / SAE J1772 & J3400. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Power + Pilot layout | Rating | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Max. EVSE I A | Min. bend R mm | Series
| EVJ 3×16 AWG + 1×18 AWG | 3×16 AWG + 1×18 AWG CP | 300 V AC | 9.6 | 52 | 118 | 13 | 58 | UL Type EVJ 300 V AC Level 1 & Light Level 2 Portable EV Cords
| EVJ 3×14 AWG + 1×18 AWG | 3×14 AWG + 1×18 AWG CP | 300 V AC | 10.8 | 78 | 152 | 18 | 65 | UL Type EVJ 300 V AC Level 1 & Light Level 2 Portable EV Cords
| EVJ 3×12 AWG + 2×18 AWG | 3×12 AWG + 2×18 AWG CP/PP | 300 V AC | 12.6 | 122 | 215 | 25 | 76 | UL Type EVJ 300 V AC Level 1 & Light Level 2 Portable EV Cords
| EV 3×10 AWG + 2×18 AWG | 3×10 AWG + 2×18 AWG CP/PP | 600 V AC | 15.8 | 188 | 335 | 35 | 95 | UL Type EV 600 V AC Level 2 Commercial & Residential Wallbox Cables
| EV 3×8 AWG + 2×18 AWG | 3×8 AWG + 2×18 AWG CP/PP | 600 V AC | 18.5 | 290 | 480 | 50 | 111 | UL Type EV 600 V AC Level 2 Commercial & Residential Wallbox Cables
| EV 3×6 AWG + 2×18 AWG | 3×6 AWG + 2×18 AWG CP/PP | 600 V AC | 21.8 | 450 | 710 | 65 | 131 | UL Type EV 600 V AC Level 2 Commercial & Residential Wallbox Cables
| EV 2×2 AWG + 1×6 AWG + 6×18 AWG | 2×2 AWG DC + 6 AWG G + 3Pr | 1000 V DC | 27.5 | 845 | 1290 | 150 | 165 | UL Type EV 1000 V DC Fast Charger (CCS1 / NACS J3400) Cables
| EV 2×1/0 AWG + 1×4 AWG + 6×18 AWG | 2×1/0 AWG DC + 4 AWG G + 3Pr | 1000 V DC | 31.2 | 1290 | 1860 | 200 | 187 | UL Type EV 1000 V DC Fast Charger (CCS1 / NACS J3400) Cables
Per NEC 625.41, continuous EV charging branch circuits are sized at 125 % of the maximum continuous EVSE load.

## Technical data
EV / EVJ UL Type EV / EVJ Thermoplastic Electric Vehicle Charging – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-type-ev-evj-thermoplastic-electric-vehicle-charging-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Article 625 / SAE J1772 & J3400. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300 V / 600–1kV (EVJ = 300 V · EV = 600 V / 1000 V)
Key data | Charging level | AC L1/L2 & DCFC (12 A to 80 A AC · up to 250 A DC)
Key data | Pilot cores | 18–16 AWG CP/PP (Control Pilot + Proximity Pilot)
Key data | Insulation/Jkt | Thermoplastic (PVC or thermoplastic TPE)
Key data | Temp. rating | −30 to +90/105°C (cold bend −30 °C or −40 °C)
Key data | Min. bend R | 6 × OD (handheld EV coupler flexing)
Electrical | Rated voltage | 300 V (Type EVJ) · 600 V or 1,000 V AC/DC (Type EV)
Electrical | Control & proximity pilot cores | 1 or 2 × 18–16 AWG (300/600 V) for SAE J1772 PWM CP & PP (+ optional pairs)
Electrical | Factory dielectric withstand test | 1,500 V AC (EVJ 300 V) · 2,500–3,000 V AC (EV 600/1000 V) for 1 min
Thermal | Continuous temperature rating | −30 °C (or −40 °C cold-bend option) to +90 °C or +105 °C dry / +60 °C wet
Thermal | Thermal cycling & overload stability | Verified thermal ageing and short-circuit withstand per standard
Mechanical | Vehicle drive-over crush test | Withstands repeated 5,000 N (1,125 lbf) tire roll-over load per UL 62 / UL
Mechanical | Minimum bending radius | 6 × OD (dynamic flexing) · 5 × OD (coiled on holster)
Resistance | Flame, oil & sunlight resistance | UL 62 FT2 (VW-1 optional), Oil Resistant I (60 °C) & 720 h Sunlight
Resistance | Environmental & chemical durability | Resistant to moisture, industrial fluids and service ageing
Standards | North American approvals | cULus UL 62 & CSA C22.2 No. 49 Listed · NEC Article 625 & CEC Section 86
Standards | Factory QA & material compliance | EN 10204 3.1 routine test certificate · RoHS 2 & REACH compliant
Identification | Surface print legend | E-File c(UL) Type EV (or EVJ) <AWG> 90C/105C 600V/300V SUN RES OIL RES FT2
Identification | Customs tariff (HS) | 8544.49 / 8544.42

## Construction
EV / EVJ UL Type EV / EVJ Thermoplastic Electric Vehicle Charging – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-type-ev-evj-thermoplastic-electric-vehicle-charging-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Article 625 / SAE J1772 & J3400. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Fine-stranded Class K bare (or tinned) copper | ASTM B172 / B174 30 AWG (0.254 mm) rope-lay power & ground cores + stranded 18–16 AWG
2 | Thermoplastic PVC or TPE primary insulation | 90 °C or 105 °C high-dielectric thermoplastic compound (Black L1, Red/White L2
3 | Low-friction talc-free separator wrap & fibrillated | Non-wicking polypropylene fillers + polyester binder tape
4 | Sunlight- & oil-resistant thermoplastic outer jacket | Smooth low-drag thermoplastic PVC or TPE compound (Black, Grey or Hi-Vis Orange)
| Type EVJ (300 V Junior · 18–12 AWG) | Compact light-duty cord for 120 V Level 1 and 240 V / 16–24 A portable EVSE cordsets
| Type EV (600 V / 1000 V Heavy Duty · 18 AWG–500 kcmil) | Full-wall thermoplastic cable for 32–80 A Level 2 wallboxes and 1000 V DC fast chargers

## Quality and supply
EV / EVJ UL Type EV / EVJ Thermoplastic Electric Vehicle Charging – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ul-type-ev-evj-thermoplastic-electric-vehicle-charging-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 62 / CSA C22.2 No. 49 / NEC Article 625 / SAE J1772 & J3400. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | UL 62 spark test, dielectric voltage-withstand & IR test — Zero breakdown at 1.5–3.0 kV AC; full pilot pair continuity verified | Every reel
Sample test | Cold bend (−30/−40 °C), vehicle crush & 720 h UV weatherometer test — No jacket cracking after cold mandrel bend; passes FT2 flame | UL follow-up audit
Standard / approval | cULus UL 62 & CSA C22.2 No. 49 Type EV / EVJ Listed
Standard / approval | NEC Article 625 & SAE J1772 / J3400 (NACS) Compliant
Standard / approval | RoHS 2 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX c(UL)us TYPE EV (or EVJ) <size> 105C 600V SUN RES OIL RES FT2
Supply | Delivery form: Non-returnable fumigated wooden or steel drums
Supply | Standard lengths: 250 m · 500 m · 1000 m standard drums
Supply | MOQ: 250 m (stock sizes) · 500 m (custom)
Supply | Lead time: 3–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP