## Request a quote
Request a quotation for EV Power + Cat5e Hybrid
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ev-charge-point-power-and-cat5e-hybrid-installation-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
EV Charge-Point Power and Cat5e Hybrid Installation Cable – Single- & three-phase dimensions & 32 A run length (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ev-charge-point-power-and-cat5e-hybrid-installation-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on BS 7671 Amendment 2 (Section 722) / BS 6724 / BS 8436 / EN 50288-2-1. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Power cores + Data sub-cable | Outer Ø ≈ mm | Weight ≈ kg/km | Clipped A | Max 32A run (≤5% ΔV) m | Series
| ConnectEV 3G4.0 + Cat5e | 3 × 4.0 mm² XLPE + Cat.5e F/UTP | 14.2 | 265 | 42 | 32 | Single-Phase 7.4 kW (3G + Cat.5e)
| ConnectEV 3G6.0 + Cat5e | 3 × 6.0 mm² XLPE + Cat.5e F/UTP | 15.6 | 345 | 54 | 48 | Single-Phase 7.4 kW (3G + Cat.5e)
| ConnectEV 3G10.0 + Cat5e | 3 × 10.0 mm² XLPE + Cat.5e F/UTP | 18.2 | 510 | 75 | 80 | Single-Phase 7.4 kW (3G + Cat.5e)
| ConnectEV 5G4.0 + Cat5e | 5 × 4.0 mm² XLPE + Cat.5e F/UTP | 16.5 | 385 | 36 | 64 | Three-Phase 11 / 22 kW (5G + Cat.5e)
| ConnectEV 5G6.0 + Cat5e | 5 × 6.0 mm² XLPE + Cat.5e F/UTP | 18.4 | 515 | 47 | 96 | Three-Phase 11 / 22 kW (5G + Cat.5e)
| ConnectEV 5G10.0 + Cat5e | 5 × 10.0 mm² XLPE + Cat.5e F/UTP | 21.8 | 780 | 65 | 160 | Three-Phase 11 / 22 kW (5G + Cat.5e)
One twisted pair in the Cat.5e can wire the CT clamp / solar diverter while the remaining pairs wire RS-485 Modbus or 100BASE-TX Ethernet.

## Technical data
EV Charge-Point Power and Cat5e Hybrid Installation Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ev-charge-point-power-and-cat5e-hybrid-installation-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on BS 7671 Amendment 2 (Section 722) / BS 6724 / BS 8436 / EN 50288-2-1. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | BS 7671 Sec. 722 (BS 6724 & EN 50288-2-1 Cat5e)
Key data | Power voltage | 0.6 / 1 kV AC (90 °C XLPE power insulation)
Key data | Power sizes | 3G4.0 to 5G10 mm (7.4 kW (32A 1P) & 22 kW (32A 3P))
Key data | Data element | Cat.5e F/UTP 4×2 (100 MHz Ethernet + CT / RS485)
Key data | Isolation voltage | 4.0 kV Test (300/500 V jacketed Cat5e sub-unit)
Key data | Outer sheath | UV-Stabilized LS (Black or Electric Blue / Green)
Electrical | Power voltage rating | 0.6 / 1 kV AC (power cores) · 300/500 V isolation on Cat.5e jacket
Electrical | Cat.5e data performance | 100 MHz bandwidth · 100 Ω ± 15 Ω impedance · 1000BASE-T / RS-485 / CT
Electrical | Power DC resistance @ 20 °C | 4.61 Ω/km (4.0) · 3.08 Ω/km (6.0) · 1.83 Ω/km (10.0) · 1.15 Ω/km (16.0)
Electrical | Clipped direct ampacity | 42 A (3G4.0) · 54 A (3G6.0) · 75 A (3G10) · 47 A (5G6.0) · 65 A (5G10)
Thermal | Max. power conductor temp. | +90 °C continuous (+250 °C short-circuit)
Thermal | Operating ambient range | -20 °C to +70 °C (fixed) · 0 °C to +50 °C (installation)
Thermal | EV continuous load factor | Sized for 1.0 continuous demand factor per BS 7671 Section 722
Mechanical | Circular outer profile | Smooth circular cross-section seals in standard M20 / M25 IP68 glands
Mechanical | Min. bend radius | 8 × overall cable OD
Mechanical | Install time saving | Cuts clip/conduit installation labour by ~45 % vs dual-cable runs
Resistance | Fire & CPR performance | BS EN 60332-1-2 · CPR Euroclass Dca / Cca-s1,d1,a1
Resistance | Low smoke & zero halogen | BS EN 61034-2 (≥ 60 % light) & BS EN 60754-1 (< 0.5 % HCl)
Resistance | Outdoor UV stability | UV-stabilized outer sheath for external building walls
Standards | UK wiring & cable standards | BS 7671 Amendment 2 (Section 722 & Reg 528.1) · BS 6724 design
Standards | Data sub-cable standard | EN 50288-2-1 / ISO/IEC 11801 Category 5e F/UTP
Standards | RoHS, REACH & CE / UKCA | 2011/65/EU RoHS 2, REACH, CE & UKCA compliant
Identification | Power core colours | 3G: Brown, Blue, GNYE · 5G: Brown, Black, Grey, Blue, GNYE
Identification | Cat.5e pair colours | Blue/White, Orange/White, Green/White, Brown/White (TIA-568)
Identification | Customs tariff (HS) | 8544.4993

## Construction
EV Charge-Point Power and Cat5e Hybrid Installation Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ev-charge-point-power-and-cat5e-hybrid-installation-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on BS 7671 Amendment 2 (Section 722) / BS 6724 / BS 8436 / EN 50288-2-1. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3G or 5G Annealed copper power conductors (4.0 to 16 mm²) | Class 2 stranded (or Class 5 flexible) plain annealed copper per BS EN 60228 (3G4.0, 3G6.0, 3G10, 5G4.0, 5G6.0, 5G10, 5G16 mm²)
2 | 90 °C GP8 Cross-Linked Polyethylene (XLPE) power insulation | Thermoset XLPE compound Type GP8 per BS 7655-1.3 (3G: Brown, Blue, Green/Yellow; 5G: Brown, Black, Grey, Blue, Green/Yellow)
3 | Integrated Screened Cat.5e F/UTP (4×2×24 AWG) data sub-cable | 4 twisted pairs of 24 AWG solid bare copper, HDPE insulation, overall aluminum/Mylar foil screen + tinned copper drain wire, and 300/500 V rated inner LSZH jacket
4 | Al/PET foil screen over Cat.5e sub-cable (100 % coverage) | Laminated aluminum/polyester tape screen with 0.5 mm tinned copper drain wire inside the Cat.5e sub-unit
5 | UV-stabilized Low-Smoke Zero-Halogen (LSZH) outer sheath | Thermoplastic halogen-free polyolefin compound Type LTS1/LTS3 per BS 7655-6.1 in Black (or Electric Blue)
| ConnectEV Single-Phase (3G4.0 / 3G6.0 / 3G10 mm² + Cat.5e) | 230 V AC single-phase L+N+PE + screened 4-pair Cat.5e for 7.4 kW (32 A) home and fleet wallboxes
| ConnectEV Three-Phase (5G4.0 / 5G6.0 / 5G10 / 5G16 mm² + Cat.5e) | 400 V AC three-phase L1+L2+L3+N+PE + screened 4-pair Cat.5e for 11 kW and 22 kW commercial EV charge points

## Quality and supply
EV Charge-Point Power and Cat5e Hybrid Installation Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ev-charge-point-power-and-cat5e-hybrid-installation-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on BS 7671 Amendment 2 (Section 722) / BS 6724 / BS 8436 / EN 50288-2-1. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3.5 kV AC power dielectric, 2.5 kV data-to-power isolation & Cat.5e sweep — Zero breakdown between power and data elements and 100 MHz Cat.5e pass | Every manufactured drum
Type test | BS EN 60332-1-2 flame, BS EN 61034-2 smoke & BS EN 60754-1 zero halogen — Light transmittance ≥ 60 % and HCl emission < 0.5 % | Type qualification
Sample test | Fluke DSX Cat.5e NEXT, return loss & attenuation verification — Passes 100 MHz Category 5e permanent-link parameters | Per production batch
Standard / approval | BS 7671 Reg 528.1 & Sec. 722
Standard / approval | BS 6724 LSZH Design
Standard / approval | CE, UKCA & CPR Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX CONNECT-EV 3G6.0mm2 0.6/1kV XLPE + SCREENED CAT5e LSZH BS 7671 CE UKCA
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP