## Request a quote
Request a quotation for EV ProInstall Cat6A SWA
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for EV ProInstall Cat6A SWA.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/armoured-lszh-ev-charge-point-power-and-cat6a-hybrid-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
EV ProInstall Cat6A SWA – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 5467 / BS 7671 & IEC 61156-5 (EV Power + Cat6A SWA). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| EV ProInstall 3G4 mm² + Cat6A SWA LSZH | 3G4 + 4×2×23AWG Cat6A | 4.0 mm² | 17.8 | 135 | 540 | 142 | Standard EV ProInstall Cat6A SWA configurations
| EV ProInstall 3G6 mm² + Cat6A SWA LSZH | 3G6 + 4×2×23AWG Cat6A | 6.0 mm² | 19.2 | 192 | 645 | 154 | Standard EV ProInstall Cat6A SWA configurations
| EV ProInstall 3G10 mm² + Cat6A SWA LSZH | 3G10 + 4×2×23AWG Cat6A | 10.0 mm² | 21.6 | 308 | 860 | 173 | Standard EV ProInstall Cat6A SWA configurations
| EV ProInstall 5G6 mm² + Cat6A SWA LSZH | 5G6 + 4×2×23AWG Cat6A | 6.0 mm² | 21.8 | 305 | 890 | 174 | Standard EV ProInstall Cat6A SWA configurations
| EV ProInstall 5G10 mm² + Cat6A SWA LSZH | 5G10 + 4×2×23AWG Cat6A | 10.0 mm² | 24.8 | 498 | 1210 | 198 | Standard EV ProInstall Cat6A SWA configurations
| EV ProInstall 5G16 mm² + Cat6A SWA LSZH | 5G16 + 4×2×23AWG Cat6A | 16.0 mm² | 27.6 | 785 | 1590 | 221 | Standard EV ProInstall Cat6A SWA configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per BS 6724 / BS 5467 / BS 7671 & IEC 61156-5 (EV Power + Cat6A SWA).

## Electrical & ampacity
EV ProInstall Cat6A SWA – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 5467 / BS 7671 & IEC 61156-5 (EV Power + Cat6A SWA). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
3G4 + 4×2×23AWG Cat6A | 4.61 | 42 | 37 | 0.57 | 11 | 3500
3G6 + 4×2×23AWG Cat6A | 3.08 | 53 | 47 | 0.86 | 7.3 | 3500
3G10 + 4×2×23AWG Cat6A | 1.83 | 73 | 65 | 1.43 | 4.4 | 3500
5G6 + 4×2×23AWG Cat6A | 3.08 | 46 | 41 | 0.86 | 6.4 | 3500
5G10 + 4×2×23AWG Cat6A | 1.83 | 63 | 56 | 1.43 | 3.8 | 3500
5G16 + 4×2×23AWG Cat6A | 1.15 | 85 | 76 | 2.29 | 2.4 | 3500
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per BS 6724 / BS 5467 / BS 7671 & IEC 61156-5 (EV Power + Cat6A SWA).

## Technical data
EV ProInstall Cat6A SWA – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 5467 / BS 7671 & IEC 61156-5 (EV Power + Cat6A SWA). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV AC (Power cores (3.5 kV AC test))
Key data | Power sizes | 3G4 to 5G16 mm² (7.4 kW (1-ph) & 11/22 kW (3-ph))
Key data | Data element | Cat6A 4×2×23AWG (500 MHz F/FTP or U/FTP screened)
Key data | Armour | Galvanized SWA (Direct burial & impact protection)
Key data | Insulation / Jkt | 90°C XLPE / LSZH (Low-smoke zero-halogen BS 6724)
Key data | Min. bend radius | 8 × D (Fixed installation & trenching)
Electrical | Power rated voltage U0/U | 0.6/1 kV AC (1,000 V RMS)
Electrical | Power routine dielectric test | 3,500 V AC for 5 minutes
Electrical | Cat6A sub-element isolation | Tested to 3.5 kV AC for BS 7671 Band I
Electrical | Cat6A impedance & bandwidth | 100 Ω ± 5 Ω · 1 to 500 MHz (10GBASE-T Class
Electrical | Max. conductor temp. (XLPE) | +90 °C continuous · +250 °C short-circuit
Thermal | Operating temperature range | -25 °C to +90 °C (power) / +75 °C (Cat6A
Thermal | Minimum installation temp. | 0 °C
Mechanical | Min. bending radius | 8 × overall diameter (D)
Mechanical | Direct burial & impact resistance | BS 6724 SWA mechanical impact protection
Resistance | Low smoke & zero halogen | BS EN 61034-2 (≥ 60 % light transmittance)
Resistance | Flame retardancy | BS EN 60332-1-2 & BS EN 60332-3-24 Cat C
Standards | Primary specification | BS 6724 / BS 5467 · BS 7671 (18th Ed.
Standards | Harmonic core colouring | BS 7671: Brown, Blue, Green/Yellow (3G) ·
Identification | Cat6A pair colours | White/Blue, White/Orange, White/Green
Identification | Outer sheath colour | Black LSZH (with optional Electric Blue

## Construction
EV ProInstall Cat6A SWA – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 5467 / BS 7671 & IEC 61156-5 (EV Power + Cat6A SWA). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 2 stranded copper power + Cat6A | IEC 60228 Class 2 plain annealed copper power cores (4–16 mm²) + 4×2×23 AWG solid bare | BS EN 60228 / IEC 61156-5
2 | 90 °C XLPE power + Foam-PE Cat6A | Cross-linked polyethylene (GP8 per BS 7655) on power cores; cellular PE + Al/PET pair | BS 6724 / ISO/IEC 11801
3 | Cat6A sub-sheath & extruded LSZH bedding | 3.5 kV voltage-segregated LSZH sub-jacket over Cat6A element + extruded LSZH inner bedding | BS 6724 / BS 7671 Reg 528.1
4 | Galvanized steel wire armour (SWA) | Single layer of galvanized round steel wires per BS EN 10257-1 (earth fault & crush | BS 6724
5 | Outer sheath (LSZH LTS1) | Low-smoke zero-halogen thermoplastic compound (LTS1 per BS 7655-6.1), Black with Blue EV | BS 6724 / EN 50575
| Single-Phase 7.4 kW Hybrid (3G4, 3G6, 3G10 + Cat6A SWA) | 3 power cores (Brown, Blue, Green/Yellow) + 4-pair screened Cat6A for 32 A single-phase EV chargers.
| Three-Phase 11/22 kW Hybrid (5G6, 5G10, 5G16 + Cat6A SWA) | 5 power cores (L1, L2, L3, N, PE) + 4-pair screened Cat6A for commercial 3-phase 22 kW EV pedestals.

## Quality and supply
EV ProInstall Cat6A SWA – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/armoured-lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 5467 / BS 7671 & IEC 61156-5 (EV Power + Cat6A SWA). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 3.5 kV AC power & Band I/II segregation test — 3,500 V AC for 5 min between power cores, Cat6A screen & SWA | 100 % of drums
Routine test | Power DC resistance & Cat6A 500 MHz sweep — BS EN 60228 Class 2 R20; ISO/IEC 11801 Class EA Cat6A | 100 % of drums
Sample test | XLPE hot-set & SWA zinc coating test — 200 °C hot-set ≤ 175 %; BS EN 10257-1 SWA wire | Per production batch
Type test | LSZH smoke density, acid gas & bunched flame — BS EN 61034-2, BS EN 60754-1 & BS EN 60332-3-24 | Type approval
Standard / approval | BS 6724 / BS 5467
Standard / approval | BS 7671 Section 722
Standard / approval | ISO/IEC 11801 Cat6A
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX EV PROINSTALL POWER + CAT6A SWA
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP