## Request a quote
Request a quotation for EV ProInstall Cat6A
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/lszh-ev-charge-point-power-and-cat6a-hybrid-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
EV ProInstall Cat6A – Unarmoured & SWA Armoured Cat.6A hybrid schedule (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 8436 / BS 7671 Sec. 722 / EN 50288-10-1 (Cat.6A). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Power cores + 500 MHz Cat.6A | Outer Ø ≈ mm | Weight ≈ kg/km | Tray/Clip A | Data class | Series
| EV ProInstall 3G6.0 + Cat6A LSZH | 3×6.0 mm² XLPE + Cat.6A S/FTP | 16.6 | 385 | 54 | 500 MHz 10GbE | Unarmoured LSZH (Power + Cat.6A S/FTP)
| EV ProInstall 5G6.0 + Cat6A LSZH | 5×6.0 mm² XLPE + Cat.6A S/FTP | 19.4 | 555 | 47 | 500 MHz 10GbE | Unarmoured LSZH (Power + Cat.6A S/FTP)
| EV ProInstall 5G10.0 + Cat6A LSZH | 5×10.0 mm² XLPE + Cat.6A S/FTP | 22.8 | 825 | 65 | 500 MHz 10GbE | Unarmoured LSZH (Power + Cat.6A S/FTP)
| EV ProInstall 5G16.0 + Cat6A LSZH | 5×16.0 mm² XLPE + Cat.6A S/FTP | 26.2 | 1190 | 87 | 500 MHz 10GbE | Unarmoured LSZH (Power + Cat.6A S/FTP)
| EV ProInstall SWA 5G6.0 + Cat6A | 5×6.0 mm² + Cat.6A S/FTP + SWA | 22.8 | 1020 | 46 | 500 MHz 10GbE | SWA Armoured LSZH (Power + Cat.6A S/FTP)
| EV ProInstall SWA 5G10.0 + Cat6A | 5×10.0 mm² + Cat.6A S/FTP + SWA | 26 | 1410 | 63 | 500 MHz 10GbE | SWA Armoured LSZH (Power + Cat.6A S/FTP)
Also available in 3G10 mm² and 4G configurations, or with dual Cat.6A S/FTP sub-cables for daisy-chained smart pedestals.

## Technical data
EV ProInstall Cat6A – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 8436 / BS 7671 Sec. 722 / EN 50288-10-1 (Cat.6A). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Standards | BS 6724 / BS 767 (& EN 50288-10-1 Cat.6A S/FTP)
Key data | Power voltage | 0.6 / 1 kV AC (90 °C XLPE power insulation)
Key data | Power sizes | 3G6.0 to 5G16 mm (7.4 kW (1P) & 11–22 kW (3P))
Key data | Data element | Cat.6A S/FTP 4×2 (500 MHz 10GBASE-T + PoE++)
Key data | EMC screening | PiMF Foil + Cu B (75 dB coupling attenuation)
Key data | Fire & CPR | LSZH Cca / B2ca (EN 50575 public building spec)
Electrical | Power voltage rating | 0.6 / 1 kV AC (power cores) · 300/500 V LSZH jacket on Cat.6A unit
Electrical | Cat.6A S/FTP performance | 500 MHz · 10GBASE-T (up to 100 m) · 100 Ω · IEEE 802.3bt Type 4 PoE++
Electrical | Power DC resistance @ 20 °C | 3.08 Ω/km (6.0) · 1.83 Ω/km (10.0) · 1.15 Ω/km (16.0)
Electrical | Clipped / tray ampacity | 54 A (3G6.0) · 75 A (3G10) · 47 A (5G6.0) · 65 A (5G10) · 87 A (5G16)
Thermal | Max. power conductor temp. | +90 °C continuous (+250 °C short-circuit)
Thermal | Operating ambient range | -20 °C to +70 °C (fixed) · 0 °C to +50 °C (installation)
Thermal | PoE++ thermal margin | 23 AWG Cat.6A S/FTP minimizes DC loop resistance under 90 W PoE++
Mechanical | Min. bend radius | 8 × overall cable OD
Mechanical | Segregation compliance | Meets BS 7671 Reg 528.1 & EN 50174-2 Cat.6A S/FTP segregation class D
Mechanical | Gland compatibility | Fits standard M20 / M25 / M32 IP68 or BS 6121 CW SWA glands
Resistance | CPR & bunched fire test | EN 50575 CPR Cca-s1a,d1,a1 (B2ca opt) & BS EN 60332-3-24
Resistance | Acid gas & smoke density | BS EN 60754-1/2 (pH ≥ 4.3, cond ≤ 2.5 µS/mm) & BS EN 61034-2 (≥ 70 %)
Resistance | UV & moisture resistance | UV-stabilized outer LSZH sheath suitable for indoor and outdoor runs
Standards | Power & wiring standards | BS 6724 · BS 8436 · BS 7671 Amendment 2 Section 722
Standards | Cat.6A data standards | EN 50288-10-1 · ISO/IEC 11801 Class EA · ANSI/TIA-568.2-D Cat.6A
Standards | RoHS, REACH & CE / UKCA | 2011/65/EU RoHS 2, REACH, CE & UKCA compliant
Identification | Power core colours | 3G: Brown, Blue, GNYE · 5G: Brown, Black, Grey, Blue, GNYE
Identification | Cat.6A pair colours | 4 × individually foil-screened pairs (TIA-568B colour code)
Identification | Customs tariff (HS) | 8544.4993

## Construction
EV ProInstall Cat6A – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 8436 / BS 7671 Sec. 722 / EN 50288-10-1 (Cat.6A). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 3G or 5G Annealed copper power conductors (6.0 to 16 mm²) | Class 2 stranded (or Class 5 flexible) plain annealed copper per BS EN 60228 (3G6.0, 3G10, 5G6.0, 5G10, 5G16 mm²)
2 | 90 °C GP8 Cross-Linked Polyethylene (XLPE) power insulation | Thermoset XLPE compound Type GP8 per BS 7655-1.3 (Brown, Black, Grey, Blue, Green/Yellow)
3 | 500 MHz Cat.6A S/FTP (4×2×23 AWG PiMF) data sub-cable | 4 twisted pairs of 23 AWG bare copper with cellular Foam-Skin PE dielectric and individual Al/PET foil per pair (PiMF)
4 | Overall tinned copper braid screen + 300/500 V LSZH sub-jacket | Tinned copper wire braid screen over the 4 PiMF pairs + 300/500 V halogen-free LSZH isolation jacket
5 | CPR Cca / B2ca Low-Smoke Zero-Halogen (LSZH) outer sheath | UV-stabilized thermoplastic halogen-free polyolefin compound Type LTS1 per BS 7655-6.1 (Unarmoured or with SWA armour)
| EV ProInstall Cat6A LSZH Unarmoured (3G6.0 to 5G16 mm² + Cat.6A S/FTP) | Halogen-free LSZH hybrid cable for indoor cable trays, basket containment and basement car park distribution
| EV ProInstall Cat6A SWA LSZH Armoured (3G6.0 to 5G16 mm² + Cat.6A S/FTP) | Galvanized Steel-Wire-Armoured BS 6724 LSZH hybrid cable for direct burial and exposed outdoor commercial EV bays

## Quality and supply
EV ProInstall Cat6A – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/lszh-ev-charge-point-power-and-cat6a-hybrid-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on BS 6724 / BS 8436 / BS 7671 Sec. 722 / EN 50288-10-1 (Cat.6A). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 3.5 kV AC power dielectric, 2.5 kV data-to-power isolation & 500 MHz sweep — Zero breakdown and full 500 MHz Class EA / Cat.6A channel compliance | Every manufactured drum
Type test | EN 50399 / BS EN 60332-3-24 CPR Cca bunched flame & smoke release test — Meets CPR Euroclass Cca-s1a,d1,a1 low-smoke zero-halogen criteria | Notified Body CPR certification
Sample test | EN 50288-10-1 coupling attenuation (≥ 75 dB) & alien crosstalk test — Zero EMI degradation when 400 V power cores carry 32–63 A EV load | Per production batch
Standard / approval | BS 6724 & BS 7671 Sec. 722
Standard / approval | EN 50288-10-1 Cat.6A S/FTP
Standard / approval | EN 50575 CPR Cca LSZH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX EV-PROINSTALL 5G6.0mm2 0.6/1kV XLPE + CAT6A S/FTP 500MHz LSZH Cca BS 6724 CE UKCA
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP