## Request a quote
Request a quotation for (F)2X(F)K2Y2YRAA / TKRA
Share system voltage, conductor cross-section, seabed depth, armour specification and installation length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/f-2x-f-k2y2yraa-tkra/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
(F)2X(F)K2Y2YRAA / TKRA 33 kV Lead-Sheathed Submarine Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2x-f-k2y2yraa-tkra/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60502-2 / CIGRE Electra 171 & 189. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| (F)2X(F)K2Y2YRAA / 3×240 mm² + FO | 3 × 240 mm² + 48F FIMT | IEC 60228 Class 2 water-blocked Cu | 118 | 26400 | 320 | 1770 | (F)2X(F)K2Y2YRAA / TKRA Construction Schedule (−20…+90 °C)
| (F)2X(F)K2Y2YRAA / 3×400 mm² + FO | 3 × 400 mm² + 48F FIMT | IEC 60228 Class 2 water-blocked Cu | 134 | 34800 | 420 | 2010 | (F)2X(F)K2Y2YRAA / TKRA Construction Schedule (−20…+90 °C)
| (F)2X(F)K2Y2YRAA / 3×630 mm² + FO | 3 × 630 mm² + 96F FIMT | IEC 60228 Class 2 water-blocked Cu | 152 | 46200 | 560 | 2280 | (F)2X(F)K2Y2YRAA / TKRA Construction Schedule (−20…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per IEC 60502-2 / CIGRE Electra 171 & 189.

## Electrical, optical & thermal p
(F)2X(F)K2Y2YRAA / TKRA 33 kV Lead-Sheathed Submarine Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2x-f-k2y2yraa-tkra/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60502-2 / CIGRE Electra 171 & 189. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 240 mm² + 48F FIMT | 0.0754 | 19/33 kV (560 A) | −20…+90 °C
3 × 400 mm² + 48F FIMT | 0.047 | 19/33 kV (710 A) | −20…+90 °C
3 × 630 mm² + 96F FIMT | 0.0283 | 19/33 kV (890 A) | −20…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
(F)2X(F)K2Y2YRAA / TKRA 33 kV Lead-Sheathed Submarine Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2x-f-k2y2yraa-tkra/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60502-2 / CIGRE Electra 171 & 189. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 19/33 kV (Tested per IEC 60502-2)
Key data | Operating temp. | −20…+90 °C (Continuous subsea & marine service)
Key data | Min. bend radius | 15 × OD (Dynamic sheave & fixed routing)
Key data | Core / conductor | 3×300–630 mm² Cu (Class 2 compacted WB Cu + 48/96F FIMT)
Key data | Outer protection | F3 Lead+SWA+PP (1.9–2.0 mm F3 lead sheath + Ø4.2 mm SWA)
Key data | Standard | IEC 60502-2 (IEC 60502-2 / CIGRE Electra 171 & 189)
Electrical | Rated voltage / transmission duty | 19/33 kV (IEC 60502-2 / CIGRE Electra 171 & 189)
Electrical | Core / conductor construction | Compacted Water-Blocked Conductors (300/630 mm²) — IEC 60228 Class 2 compacted copper filled with semiconductive water-blocking compound
Electrical | Primary dielectric / buffering | 36 kV XLPE & Phase ID Swelling Tapes — 8.0 mm triple-extruded XLPE + Red/Blue/Yellow phase tapes + semicon swelling tape
Thermal | Continuous operating temperature | −20…+90 °C (subsea, marine & submersible duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per IEC 60502-2 / CIGRE Electra 171 & 189
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Galvanized Steel Armour (R) & PP Serving (AA) — 83–98 × Ø4.2 mm galvanized steel wires + bitumen-impregnated PP yarn outer serving
Mechanical | Minimum bending radius | 15 × OD
Mechanical | Hydrostatic, tensile & crush duty | AISI 316L Optical Unit (48 / 96 SM Fibres) — Laser-welded stainless-steel tube (Ø 3.7 mm) with semiconducting PE oversheath
Resistance | Hydrostatic pressure & water blocking | Engineered for continuous submersion and hydrostatic integrity per IEC 60502-2 / CIGRE Electra 171 & 189
Resistance | Seawater, oil & chemical resistance | Resistant to seawater hydrolysis, hydraulic oils and abrasion per IEC 60502-2 / CIGRE Electra 171 & 189
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEC 60502-2 / CIGRE Electra 171 & 189
Standards | Environmental & test standards | IEC 60228 / IEC 60332 / ISO 13628-5 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | (F)2X(F)K2Y2YRAA / TKRA
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (F3 Lead + SWA + PP)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
(F)2X(F)K2Y2YRAA / TKRA 33 kV Lead-Sheathed Submarine Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2x-f-k2y2yraa-tkra/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60502-2 / CIGRE Electra 171 & 189. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Compacted Water-Blocked Conductors (300/630 mm²) | IEC 60228 Class 2 compacted copper filled with semiconductive water-blocking compound
2 | 36 kV XLPE & Phase ID Swelling Tapes | 8.0 mm triple-extruded XLPE + Red/Blue/Yellow phase tapes + semicon swelling tape
3 | Extruded F3 Lead-Alloy Sheath (K, 1.9–2.0 mm) | 100% impervious radial metallic moisture barrier + semiconducting PE phase sheath
4 | AISI 316L Optical Unit (48 / 96 SM Fibres) | Laser-welded stainless-steel tube (Ø 3.7 mm) with semiconducting PE oversheath
5 | Galvanized Steel Armour (R) & PP Serving (AA) | 83–98 × Ø4.2 mm galvanized steel wires + bitumen-impregnated PP yarn outer serving
| (F)2X(F)K2Y2YRAA / TKRA — Standard Subsea & Marine Execution | Built to IEC 60502-2 / CIGRE Electra 171 & 189 with compacted water-blocked conductors (300/630 mm²) and galvanized steel armour (r) & pp serving (aa)
| (F)2X(F)K2Y2YRAA / TKRA — Custom Drum Length & Termination Kit | Available in custom continuous subsea/wellbore drum lengths or pre-terminated assemblies
| (F)2X(F)K2Y2YRAA / TKRA — Routine & Hydrostatic Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & pressure/dimensional report

## Quality and supply
(F)2X(F)K2Y2YRAA / TKRA 33 kV Lead-Sheathed Submarine Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2x-f-k2y2yraa-tkra/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on IEC 60502-2 / CIGRE Electra 171 & 189. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (IEC 60502-2 / CIGRE Electra 171 & 189) — DC resistance at 20 °C / optical attenuation and outer diameter within IEC 60502-2 / CIGRE Electra 171 & 189 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (IEC 60502-2 / CIGRE Electra 171 & 189) — Zero dielectric breakdown and verified insulation resistance for 19/33 kV rating | Every manufactured drum length
Type test | Hydrostatic pressure, water-blocking & mechanical endurance qualification (IEC 60502-2 / CIGRE Electra 171 & 189) — Verified submersion integrity, tensile load and thermal stability across −20…+90 °C | Type qualification & periodic lot audit
Standard / approval | IEC 60502-2 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (F)2X(F)K2Y2YRAA / TKRA IEC 60502-2 19/33 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel subsea reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous subsea/wellbore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP