## Request a quote
Request a quotation for (F)2XS(FL)2YRAA
Share system voltage, conductor cross-section, seabed depth, armour specification and installation length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/f-2xs-fl-2yraa/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
(F)2XS(FL)2YRAA 19/33 kV Offshore Wind Inter-Array Cable – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2xs-fl-2yraa/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Tensile rating kN ≈ | Min. bend R mm | Series
| (F)2XS(FL)2YRAA 3×240 mm² + FO | 3 × 240 mm² + 48F FIMT | IEC 60228 Class 2 water-blocked Cu | 118 | 26400 | 320 | 1770 | (F)2XS(FL)2YRAA Construction Schedule (−20…+90 °C)
| (F)2XS(FL)2YRAA 3×400 mm² + FO | 3 × 400 mm² + 48F FIMT | IEC 60228 Class 2 water-blocked Cu | 134 | 34800 | 420 | 2010 | (F)2XS(FL)2YRAA Construction Schedule (−20…+90 °C)
| (F)2XS(FL)2YRAA 3×630 mm² + FO | 3 × 630 mm² + 96F FIMT | IEC 60228 Class 2 water-blocked Cu | 152 | 46200 | 560 | 2280 | (F)2XS(FL)2YRAA Construction Schedule (−20…+90 °C)
Custom core cross-sections, pair/fibre counts, armour grades and factory drum lengths available per DIN VDE 0276-620 / IEC 60502-2.

## Electrical, optical & thermal p
(F)2XS(FL)2YRAA 19/33 kV Offshore Wind Inter-Array Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2xs-fl-2yraa/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Impedance | Operating temp.
3 × 240 mm² + 48F FIMT | 0.0754 | 19/33 kV (560 A) | −20…+90 °C
3 × 400 mm² + 48F FIMT | 0.047 | 19/33 kV (710 A) | −20…+90 °C
3 × 630 mm² + 96F FIMT | 0.0283 | 19/33 kV (890 A) | −20…+90 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric or OTDR continuity and dimensional verification.

## Technical data
(F)2XS(FL)2YRAA 19/33 kV Offshore Wind Inter-Array Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2xs-fl-2yraa/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 19/33 kV (Tested per VDE 0276-620)
Key data | Operating temp. | −20…+90 °C (Continuous subsea & marine service)
Key data | Min. bend radius | 15 × OD (Dynamic sheave & fixed routing)
Key data | Core / conductor | 3×240–630 mm² Cu (Class 2 water-blocked copper + FIMT)
Key data | Outer protection | Al-PE + SWA + PP (Radial Al-PE moisture barrier)
Key data | Standard | VDE 0276-620 (DIN VDE 0276-620 / IEC 60502-2)
Electrical | Rated voltage / transmission duty | 19/33 kV (DIN VDE 0276-620 / IEC 60502-2)
Electrical | Core / conductor construction | Water-Blocked Phase Cores (3×500 mm²) — Class 2 longitudinal water-blocked Cu (F) + semicon + 8.0 mm 36 kV XLPE (2X)
Electrical | Primary dielectric / buffering | Cu Wire Screen & Al-PE Laminate S(FL)2Y>c< — 25 mm² Cu wire/tape screen + swelling powder (FL) + Al foil laminate + HDPE sheath
Thermal | Continuous operating temperature | −20…+90 °C (subsea, marine & submersible duty)
Thermal | Short-circuit / peak thermal rating | Verified thermal stability per DIN VDE 0276-620 / IEC 60502-2
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel drum
Mechanical | Outer protection / armouring | Hessian & PP Roving Outer Serving (AA) — Two bitumen-impregnated Hessian tapes + black/yellow polypropylene yarn serving
Mechanical | Minimum bending radius | 15 × OD
Mechanical | Hydrostatic, tensile & crush duty | Galvanized Round Steel Wire Armour (R) — 54–68 × Ø4.0–4.75 mm galvanized steel wires embedded in bitumen over bedding
Resistance | Hydrostatic pressure & water blocking | Engineered for continuous submersion and hydrostatic integrity per DIN VDE 0276-620 / IEC 60502-2
Resistance | Seawater, oil & chemical resistance | Resistant to seawater hydrolysis, hydraulic oils and abrasion per DIN VDE 0276-620 / IEC 60502-2
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | DIN VDE 0276-620 / IEC 60502-2
Standards | Environmental & test standards | IEC 60228 / IEC 60332 / ISO 13628-5 / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | (F)2XS(FL)2YRAA
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Al-PE + SWA + PP)
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
(F)2XS(FL)2YRAA 19/33 kV Offshore Wind Inter-Array Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2xs-fl-2yraa/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Water-Blocked Phase Cores (3×500 mm²) | Class 2 longitudinal water-blocked Cu (F) + semicon + 8.0 mm 36 kV XLPE (2X)
2 | Cu Wire Screen & Al-PE Laminate S(FL)2Y>c< | 25 mm² Cu wire/tape screen + swelling powder (FL) + Al foil laminate + HDPE sheath
3 | Integrated Subsea FO Cable & PP Fillers | Armoured single-mode optical cable unit(s) + polypropylene string fillers in valleys
4 | Galvanized Round Steel Wire Armour (R) | 54–68 × Ø4.0–4.75 mm galvanized steel wires embedded in bitumen over bedding
5 | Hessian & PP Roving Outer Serving (AA) | Two bitumen-impregnated Hessian tapes + black/yellow polypropylene yarn serving
| (F)2XS(FL)2YRAA — Standard Subsea & Marine Execution | Built to DIN VDE 0276-620 / IEC 60502-2 with water-blocked phase cores (3×500 mm²) and hessian & pp roving outer serving (aa)
| (F)2XS(FL)2YRAA — Custom Drum Length & Termination Kit | Available in custom continuous subsea/wellbore drum lengths or pre-terminated assemblies
| (F)2XS(FL)2YRAA — Routine & Hydrostatic Test Certified | Supplied with EN 10204 3.1 routine dielectric, resistance & pressure/dimensional report

## Quality and supply
(F)2XS(FL)2YRAA 19/33 kV Offshore Wind Inter-Array Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/f-2xs-fl-2yraa/ ¦ Data revision 2026-10-25
Typical values for this cable type, based on DIN VDE 0276-620 / IEC 60502-2. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance, continuity & dimensional verification (DIN VDE 0276-620 / IEC 60502-2) — DC resistance at 20 °C / optical attenuation and outer diameter within DIN VDE 0276-620 / IEC 60502-2 tolerances | Every manufactured drum length
Routine test | High-voltage dielectric & insulation resistance test (DIN VDE 0276-620 / IEC 60502-2) — Zero dielectric breakdown and verified insulation resistance for 19/33 kV rating | Every manufactured drum length
Type test | Hydrostatic pressure, water-blocking & mechanical endurance qualification (DIN VDE 0276-620 / IEC 60502-2) — Verified submersion integrity, tensile load and thermal stability across −20…+90 °C | Type qualification & periodic lot audit
Standard / approval | VDE 0276-620 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX (F)2XS(FL)2YRAA VDE 0276-620 19/33 kV CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums or steel subsea reels
Supply | Standard lengths: 500 m, 1,000 m or custom continuous subsea/wellbore lengths
Supply | MOQ: 100 m (standard configurations) · 500 m (custom builds)
Supply | Lead time: 2–5 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP