## Request a quote
Request a quotation for FAA L-824 Type B
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/faa-l-824-type-b-airfield-lighting-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
FAA L-824 Type B Airfield Lighting Cable – Dimensions, wall thickness & weight (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/faa-l-824-type-b-airfield-lighting-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on FAA AC 150/5345-7F / ICEA S-93-639 (NEMA WC 74). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | FAA designation | Conductor & shield | EPR / CPE wall mm | Nominal Ø mm | Weight ≈ kg/km | Max. DC R Ω/km | Series
| L-824 Type B 8 AWG 5kV NS | 8 AWG (8.37 mm²) 7/19W · Unshielded | 2.80 / 1.14 | 12.2 | 195 | 2.14 | 5 kV L-824 Type B Non-Shielded
| L-824 Type B 6 AWG 5kV NS | 6 AWG (13.3 mm²) 7/19W · Unshielded | 2.80 / 1.14 | 13.2 | 255 | 1.35 | 5 kV L-824 Type B Non-Shielded
| L-824 Type B 8 AWG 5kV SH | 8 AWG (8.37 mm²) · 5 mil Cu Shield | 2.80 / 1.52 | 14.5 | 285 | 2.14 | 5 kV L-824 Type B Copper-Tape Shielded
| L-824 Type B 6 AWG 5kV SH | 6 AWG (13.3 mm²) · 5 mil Cu Shield | 2.80 / 1.52 | 15.5 | 355 | 1.35 | 5 kV L-824 Type B Copper-Tape Shielded
8 AWG is standard for 6.6 A series loops; 6 AWG is used for 20 A high-intensity runway loops or extra-long vault home runs.

## Technical data
FAA L-824 Type B Airfield Lighting Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/faa-l-824-type-b-airfield-lighting-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on FAA AC 150/5345-7F / ICEA S-93-639 (NEMA WC 74). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | FAA specification | AC 150/5345-7F (L-824 Type B (ICEA S-93-639))
Key data | Voltage rating | 5,000 V (5 kV) (6.6 A & 20 A CCR primary loop)
Key data | Standard sizes | 8 AWG & 6 AWG (7- or 19-strand bare/tinned Cu)
Key data | Insulation / Jacke | EPR / CPE (CSP) (2.80 mm EPR + 1.14–1.52 mm CPE)
Key data | Shield options | Non-Shielded / C (5 mil Copper tape shield opt.)
Key data | Temperature | +90 °C Continuou (+130 °C overload · +250 °C SC)
Electrical | Rated voltage & circuit | 5,000 V (5 kV, 100 % level) for 6.6 A & 20 A CCR series loops
Electrical | AC & DC factory test | 18 kV AC (5 min) or 35 kV DC (15 min) + partial discharge ≤ 5 pC
Electrical | Max. DC resistance @ 20 °C | 2.14 Ω/km (8 AWG / 8.37 mm²) · 1.35 Ω/km (6 AWG / 13.3 mm²)
Electrical | Insulation resistance | K ≥ 20,000 MΩ·1000 ft at 15.6 °C
Thermal | Continuous conductor temp. | +90 °C normal operation
Thermal | Emergency overload temp. | +130 °C (max. 100 hours/year)
Thermal | Short-circuit temperature | +250 °C
Mechanical | EPR insulation wall | 2.80 mm (110 mil) nominal on 5 kV 8 AWG & 6 AWG
Mechanical | CPE jacket wall | 1.14 mm (45 mil non-shielded) · 1.52 mm (60 mil shielded)
Mechanical | Min. bend radius | 8 × OD (non-shielded) · 12 × OD (copper-tape shielded)
Resistance | Ozone & corona resistance | Passes ICEA 0.03 % ozone chamber test without cracking
Resistance | Moisture & direct burial | Approved for direct burial in soil, sand and submerged conduit
Resistance | De-icer & Jet-A fuel | Thermoset CPE jacket resists runway potassium acetate & Jet-A spills
Standards | FAA specification | FAA Advisory Circular AC 150/5345-7F (L-824 Type B)
Standards | ICEA / NEMA standard | ICEA S-93-639 / NEMA WC 74
Standards | Connector compatibility | Fits FAA AC 150/5345-26 L-823 plug & receptacle kits
Identification | Surface print legend | FAA L-824 TYPE B 5000V 8 AWG (or 6 AWG) EPR/CPE + Year + Mfr
Identification | Customs tariff (HS) | 8544.6010
Identification | Sequential footage marks | Printed every 2 ft (0.61 m) along outer jacket

## Construction
FAA L-824 Type B Airfield Lighting Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/faa-l-824-type-b-airfield-lighting-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on FAA AC 150/5345-7F / ICEA S-93-639 (NEMA WC 74). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 8 AWG or 6 AWG Class B/C stranded copper conductor | 7-strand Class B or 19-strand Class C soft annealed bare or tinned copper per ASTM B3 / B8 / B33
2 | Extruded semiconducting conductor stress control layer | Smooth semiconducting thermoset layer extruded over the stranded copper conductor
3 | 110 mil (2.80 mm) 90 °C EPR (Ethylene Propylene Rubber) insulation | Ozone-resistant, tree-retardant 90 °C EPR thermoset dielectric (100 % insulation level, 2.80 mm nominal wall)
4 | Helically applied copper tape shield (on Shielded Type B) | Optional semiconducting insulation screen + 0.127 mm (5 mil) bare/tinned copper tape with ≥ 15 % overlap
5 | Heavy-duty Black CPE / CSP thermoset elastomer outer jacket | 1.14 mm (45 mil, non-shielded) or 1.52 mm (60 mil, shielded) Chlorinated Polyethylene (CPE) / CSP jacket
| L-824 Type B Non-Shielded (8 AWG / 6 AWG · 5 kV EPR/CPE) | Unshielded 5 kV EPR-insulated, CPE-jacketed airfield primary cable compatible with standard L-823 field-moulded/crimp connectors
| L-824 Type B Shielded (8 AWG / 6 AWG · 5 kV EPR/Cu-Tape/CPE) | Copper-tape-shielded 5 kV EPR/CPE airfield primary cable for lightning-prone airfields and EMI protection near NAVAID cables

## Quality and supply
FAA L-824 Type B Airfield Lighting Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/faa-l-824-type-b-airfield-lighting-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on FAA AC 150/5345-7F / ICEA S-93-639 (NEMA WC 74). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 18 kV AC dielectric withstand & partial discharge (< 5 pC) test — Zero breakdown for 5 min and PD extinction above operating stress | Every manufactured reel
Type test | ICEA S-93-639 ozone resistance, hot creep & water absorption test — Zero ozone cracking and stable dielectric constant in 90 °C water | Qualification test
Sample test | L-823 connector fit & dimensional wall thickness verification — Matches FAA AC 150/5345-26 L-823 Style 3/10 connector bore diameters | Every production batch
Standard / approval | FAA AC 150/5345-7F L-824 Type B
Standard / approval | ICEA S-93-639 / NEMA WC 74
Standard / approval | ICAO Annex 14 Compatible
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX FAA L-824 TYPE B 8 AWG 5000V EPR/CPE ICEA S-93-639
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP