## Request a quote
Request a quotation for FAA L-824 Type C
Application engineer · power & MV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/faa-l-824-type-c-airfield-lighting-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
FAA L-824 Type C Airfield Lighting Cable – 5 kV Primary & 600 V Secondary schedule (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/faa-l-824-type-c-airfield-lighting-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on FAA AC 150/5345-7F / ICEA S-95-658 (NEMA WC 70) / S-93-639. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | FAA designation | Conductors & shield | XLPE wall mm | Nominal Ø mm | Weight ≈ kg/km | Max. DC R Ω/km | Series
| L-824 Type C 8 AWG 5kV NS | 1 × 8 AWG (7/19W Cu) · Single-Wall XLPE | 2.80 (110 mil) | 9.8 | 135 | 2.14 | 5 kV L-824 Type C Primary Cable
| L-824 Type C 6 AWG 5kV NS | 1 × 6 AWG (7/19W Cu) · Single-Wall XLPE | 2.80 (110 mil) | 10.8 | 185 | 1.35 | 5 kV L-824 Type C Primary Cable
| L-824 Type C 8 AWG 5kV SH | 1 × 8 AWG · XLPE + 5 mil Cu Shield + Jacket | 2.80 + 1.52 | 14.2 | 265 | 2.14 | 5 kV L-824 Type C Primary Cable
| L-824 Type C 6 AWG 5kV SH | 1 × 6 AWG · XLPE + 5 mil Cu Shield + Jacket | 2.80 + 1.52 | 15.2 | 335 | 1.35 | 5 kV L-824 Type C Primary Cable
| L-824 Type C 2×12 AWG 600V | 2 × 12 AWG (19W Cu) · 600 V Secondary | 1.14 + 1.52 | 11.4 | 160 | 5.43 | 600 V L-824 Type C Secondary Lead
Non-shielded 8 AWG Type C has a compact 9.8 mm OD, allowing multiple circuits to share 2-inch PVC airfield ducts with low pulling tension.

## Technical data
FAA L-824 Type C Airfield Lighting Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/faa-l-824-type-c-airfield-lighting-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on FAA AC 150/5345-7F / ICEA S-95-658 (NEMA WC 70) / S-93-639. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | FAA specification | AC 150/5345-7F (L-824 Type C XLPE Series)
Key data | Voltage classes | 5,000 V & 600 V (5 kV CCR loop + 600 V lamp lead)
Key data | Primary sizes | 8 AWG & 6 AWG (7- or 19-strand bare/tinned Cu)
Key data | Insulation | 90 °C XLPE (2.80 mm (110 mil) 5 kV wall)
Key data | Constructions | Unshielded / Cu- (Single-wall XLPE or Cu-shield+PE)
Key data | Temperature | +90 °C Wet / Dry (+130 °C overload · +250 °C SC)
Electrical | Voltage ratings | 5,000 V (1C primary CCR series) · 600 V (2C secondary fixture lead)
Electrical | Factory dielectric test | 18 kV AC for 5 min (5 kV primary) · 3.5 kV AC (600 V secondary)
Electrical | Max. DC resistance @ 20 °C | 2.14 Ω/km (8 AWG) · 1.35 Ω/km (6 AWG) · 5.43 Ω/km (12 AWG)
Electrical | Insulation resistance | ≥ 10,000 MΩ·km @ 20 °C
Thermal | Continuous conductor temp. | +90 °C Wet or Dry
Thermal | Emergency overload temp. | +130 °C
Thermal | Short-circuit temperature | +250 °C (5 s)
Mechanical | 5 kV XLPE wall thickness | 2.80 mm (110 mil) minimum average wall
Mechanical | Min. bend radius | 6 × OD (non-shielded single-wall) · 12 × OD (copper-tape shielded)
Mechanical | Duct pulling coefficient | Low-friction cross-linked XLPE reduces tension on long conduit pulls
Resistance | Water & direct burial | Approved for direct earth burial, underground ducts and wet base cans
Resistance | Sunlight & weather | Carbon-black stabilized XLPE passes UL/ICEA weatherometer tests
Resistance | Hot creep & deformation | Thermoset cross-linking passes ICEA +150 °C hot-set test
Standards | FAA specification | FAA Advisory Circular AC 150/5345-7F (L-824 Type C)
Standards | ICEA / NEMA standards | ICEA S-95-658 (NEMA WC 70) & ICEA S-93-639 (NEMA WC 74)
Standards | ETL / Third-party cert. | Intertek ETL Verified to FAA AC 150/5345-7F available
Identification | Surface print legend | FAA L-824 TYPE C 5000V 8 AWG XLPE ICEA S-95-658 + Year + Footage
Identification | Customs tariff (HS) | 8544.6010
Identification | Colour coding Options | Black standard; Red, Blue, White or Yellow co-extruded stripes for multi-circuit vaults

## Construction
FAA L-824 Type C Airfield Lighting Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/faa-l-824-type-c-airfield-lighting-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on FAA AC 150/5345-7F / ICEA S-95-658 (NEMA WC 70) / S-93-639. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 7- or 19-strand annealed bare or tinned copper conductor | 8 AWG (8.37 mm²) or 6 AWG (13.3 mm²) Class B (7W) or Class C (19W) copper per ASTM B3 / B8 / B33
2 | Extruded semiconducting XLPE conductor screen (5 kV) | Thermoset semiconducting cross-linked layer bonded over the stranded conductor
3 | 110 mil (2.80 mm) 90 °C Cross-Linked Polyethylene (XLPE) | Sunlight-resistant carbon-black-filled thermoset XLPE serving as combined insulation and jacket on Non-Shielded Type C
4 | Optional helically applied copper tape shield (Shielded Type C) | Semiconducting insulation screen + 0.127 mm (5 mil) overlapped bare/tinned copper tape shield
5 | Single-wall XLPE surface or outer PE/CPE jacket (Shielded) | Integral weather-resistant Black XLPE outer wall (Non-Shielded) or 1.14–1.52 mm PE/CPE outer jacket over copper shield | Dimensioned for FAA L-823 primary connector kits
| L-824 Type C 5 kV Non-Shielded (8 AWG / 6 AWG Single-Wall XLPE) | Most widely installed FAA 5 kV runway primary cable: conductor screen + 110 mil (2.80 mm) black XLPE per ICEA S-95-658
| L-824 Type C 5 kV Shielded (8 AWG / 6 AWG XLPE + Cu Tape + Jacket) | Copper-tape-shielded 5 kV XLPE primary cable with outer protective jacket per ICEA S-93-639
| L-824 Type C 600 V Secondary (2×12 AWG / 2×10 AWG) | 2-conductor 600 V XLPE/CPE secondary tail connecting the L-830 transformer secondary to the L-823 two-pole lamp plug

## Quality and supply
FAA L-824 Type C Airfield Lighting Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/faa-l-824-type-c-airfield-lighting-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on FAA AC 150/5345-7F / ICEA S-95-658 (NEMA WC 70) / S-93-639. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 18 kV AC dielectric test, spark test & DC resistance — Zero breakdown for 5 min and DC resistance within ASTM B8 limits | Every manufactured reel
Type test | ICEA S-95-658 hot-creep, water absorption & cold bend (-40 °C) — Hot-set elongation ≤ 100 % and zero cracking at -40 °C | Qualification test
Sample test | Semiconducting conductor screen strip & L-823 connector gauge check — Clean stripping for field L-823 termination and exact OD fit | Per production batch
Standard / approval | FAA AC 150/5345-7F L-824 Type C
Standard / approval | ICEA S-95-658 / NEMA WC 70
Standard / approval | ICEA S-93-639 (Shielded)
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX FAA L-824 TYPE C 8 AWG 5000V XLPE ICEA S-95-658
Supply | Delivery form: Fumigated wooden drums or steel export reels
Supply | Standard lengths: 500 m · 1000 m (or custom cut lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP