## Request a quote
Request a quotation for FDEFP 1.8/3 kV Screened
Share core count × cross-section (mm² or AWG), screened/unscreened build, required torsion rating (±100°/m to ±450°/0.5m), minimum temperature (−40 or −50 °C) and length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/fdefp-1-8-3kv-screened-epr-cr-torsion-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
FDEFP 1.8/3 kV (0.6/1 kV) GB/T 29631 Tinned-Copper Braid Screened EPR/ – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fdefp-1-8-3kv-screened-epr-cr-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Max. pulling kN ≈ | Min. bend R mm | Series
| FDEFP 1.8 7G1.5 mm² | 7G1.5 mm² (or 7C × 16 AWG) | IEC 60228 Class 5/6 / Class K Cu | 11.4 | 215 | 2.4 | 70 | FDEFP 1.8/3 kV Screened Construction Schedule (−40…+90 °C)
| FDEFP 1.8 12G1.5 mm² | 12G1.5 mm² (or 12C × 16 AWG) | IEC 60228 Class 5/6 / Class K Cu | 14.8 | 345 | 4.1 | 90 | FDEFP 1.8/3 kV Screened Construction Schedule (−40…+90 °C)
| FDEFP 1.8 18G2.5 mm² | 18G2.5 mm² (or 18C × 14 AWG) | IEC 60228 Class 5/6 / Class K Cu | 19.6 | 680 | 9.8 | 120 | FDEFP 1.8/3 kV Screened Construction Schedule (−40…+90 °C)
Custom conductor cross-sections, core counts, pre-lugged tower kits and drum lengths available per GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard.

## Electrical & thermal parameters
FDEFP 1.8/3 kV (0.6/1 kV) GB/T 29631 Tinned-Copper Braid Screened EPR/ – Electrical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fdefp-1-8-3kv-screened-epr-cr-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ Ω/km | Rating / Impedance | Operating temp.
7G1.5 mm² (or 7C × 16 AWG) | 13.3 | 1.8/3 kV (0.6/1 kV) (18 A) | −40…+90 °C
12G1.5 mm² (or 12C × 16 AWG) | 13.3 | 1.8/3 kV (0.6/1 kV) (16 A) | −40…+90 °C
18G2.5 mm² (or 18C × 14 AWG) | 7.98 | 1.8/3 kV (0.6/1 kV) (24 A) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, AC high-voltage spark/dielectric and dimensional verification.

## Technical data
FDEFP 1.8/3 kV (0.6/1 kV) GB/T 29631 Tinned-Copper Braid Screened EPR/ – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/fdefp-1-8-3kv-screened-epr-cr-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 1.8/3 kV (0.6/1 (Tested per GB/T 29631 / NB/T 31034)
Key data | Operating temp. | −40…+90 °C (Cold-climate & nacelle wind service)
Key data | Min. bend radius | 6 × OD (Drip-loop, hub & tower routing)
Key data | Core / conductor | Class 5 Flexible (Stranded flexible copper conductors rate)
Key data | Outer protection | Polychloroprene (Oil-, salt-spray- and torsion-resistant )
Key data | Standard | GB/T 29631 / NB/ (GB/T 29631 & NB/T 31034 FDEFP EMC-Screen)
Electrical | Rated voltage / operating system | 1.8/3 kV (0.6/1 kV) (GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard)
Electrical | Core / conductor construction | Class 5 Flexible Copper / Tinned Copper Cores — Stranded flexible copper conductors rated up to 1.8/3 kV
Electrical | Primary dielectric / insulation | EPR Primary Core Insulation (Code E) — High-dielectric ethylene-propylene rubber insulation
Thermal | Continuous operating temperature | −40…+90 °C (wind turbine nacelle, hub & tower duty)
Thermal | Low-temperature torsion & cold bend | Verified cold-flex and torsion endurance across −40…+90 °C per GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel cable drum
Mechanical | Outer jacket / sheath protection | Polychloroprene (CR) / CSM Outer Sheath (Code F) — Oil-, salt-spray- and torsion-resistant heavy rubber jacket
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Intermediate screen / separator / core layer | Tinned Copper Wire Braid Screen (Code P) — High-coverage braided tinned copper EMC shield
Resistance | Oil, grease, ozone & UV resistance | Resistant to wind turbine gearbox oil, hydraulic fluid, ozone and UV weathering per GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard
Resistance | Flame retardancy & smoke/halogen emission | Flame-retardant and environmental performance verified per GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard
Standards | Conductor & flame/test standards | IEC 60228 / IEC 60332-1-2 & -3 / UL 2277 WTTC / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | FDEFP 1.8/3 kV Screened
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Polychloroprene )
Identification | Customs tariff (HS) | 8544.49 / 8544.60

## Construction
FDEFP 1.8/3 kV (0.6/1 kV) GB/T 29631 Tinned-Copper Braid Screened EPR/ – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/fdefp-1-8-3kv-screened-epr-cr-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 Flexible Copper / Tinned Copper | Stranded flexible copper conductors rated up to 1.8/3 kV
2 | EPR Primary Core Insulation (Code E) | High-dielectric ethylene-propylene rubber insulation
3 | Tinned Copper Wire Braid Screen (Code P) | High-coverage braided tinned copper EMC shield
4 | Polychloroprene (CR) / CSM Outer Sheath | Oil-, salt-spray- and torsion-resistant heavy rubber jacket
| FDEFP 1.8/3 kV Screened — Standard Wind Turbine Execution | Built to GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard with class 5 flexible copper / tinned copper cores and polychloroprene (cr) / csm outer sheath (code f)
| FDEFP 1.8/3 kV Screened — Pre-Cut Tower / Drip-Loop Kit | Available on bulk export reels or pre-cut to turbine tower section and nacelle drip-loop lengths
| FDEFP 1.8/3 kV Screened — Cold Torsion & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, conductor DC resistance & cold-torsion qualification report

## Quality and supply
FDEFP 1.8/3 kV (0.6/1 kV) GB/T 29631 Tinned-Copper Braid Screened EPR/ – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/fdefp-1-8-3kv-screened-epr-cr-torsion-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard) — DC resistance at 20 °C and insulation/sheath wall thickness within GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard limits | Every manufactured drum length
Routine test | AC high-voltage dielectric & insulation resistance test (GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard) — Zero dielectric breakdown and verified insulation resistance for 1.8/3 kV (0.6/1 kV) rating | Every manufactured drum length
Type test | Low-temperature drip-loop torsion, oil & flame qualification (GB/T 29631 & NB/T 31034 FDEFP EMC-Screened EPR/CR Wind Torsion Cable Standard) — Verified cold torsion cycle endurance, oil resistance and flame retardancy across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | GB/T 29631 / NB/T 31034 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX FDEFP 1.8/3 kV Screened GB/T 29631 / NB/T 31034 1.8/3 kV (0.6/1 kV) CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel reels or pre-cut wind turbine tower & drip-loop kits
Supply | Standard lengths: 500 m, 1,000 m or custom cut-to-length nacelle drip-loop and tower section sets
Supply | MOQ: 100 m (standard configurations) · 300 m (custom wind builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP