## Request a quote
Request a quotation for FEP Hook-Up Wire (NEMA HP 4 / UL)
Application engineer · Fluoropolymer hook-up wires
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/fep-high-temperature-hook-up-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
FEP High-Temperature Hook-Up Wire (NEMA HP 4 & UL 1330 / 1332 / 10203) – Dimensions, voltage & electrical (17)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fep-high-temperature-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ANSI/NEMA HP 4 & UL 758. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Style · AWG size | Rated voltage | Temp. rating | Stranding (count/AWG) | CSA ≈ mm² | Cond. Ø mm | FEP wall mm | Nominal OD mm | Mass ≈ kg/km | Max. DC res. (20 °C) Ω/km | Series
| NEMA HP 4 Type KT · 28 AWG | 250 V | 150/200 °C | 7/36 | 0.089 | 0.38 | 0.15 | 0.69 | 1.3 | 213 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type KT · 24 AWG | 250 V | 150/200 °C | 19/36 | 0.241 | 0.61 | 0.15 | 0.91 | 2.9 | 84 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type KT · 20 AWG | 250 V | 150/200 °C | 19/32 | 0.616 | 0.97 | 0.15 | 1.27 | 6.5 | 32.3 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type K · 24 AWG | 600 V | 150/200 °C | 19/36 | 0.241 | 0.61 | 0.25 | 1.12 | 3.6 | 84 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type K · 22 AWG | 600 V | 150/200 °C | 19/34 | 0.382 | 0.76 | 0.25 | 1.27 | 5.1 | 52.5 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type K · 20 AWG | 600 V | 150/200 °C | 19/32 | 0.616 | 0.97 | 0.25 | 1.47 | 7.4 | 32.3 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type K · 16 AWG | 600 V | 150/200 °C | 19/29 | 1.23 | 1.37 | 0.25 | 1.96 | 14.1 | 15.8 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type K · 12 AWG | 600 V | 150/200 °C | 19/25 | 3.08 | 2.18 | 0.25 | 2.74 | 31.8 | 6.3 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type KK · 20 AWG | 1,000 V | 150/200 °C | 19/32 | 0.616 | 0.97 | 0.38 | 1.73 | 9.1 | 32.3 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| NEMA HP 4 Type KK · 14 AWG | 1,000 V | 150/200 °C | 19/27 | 1.94 | 1.7 | 0.38 | 2.46 | 22.8 | 9.9 | ANSI/NEMA HP 4-2021 · Types KT (250 V), K (600 V) & KK (1,000 V)
| UL AWM 1332 · 24 AWG | 300 Vac | 200 °C | 7/32 | 0.22 | 0.61 | 0.33 | 1.27 | 4 | 89.4 | UL 758 AWM · Style 1332 (300 Vac), Style 1330 (600 Vac) & Style 10203 (1,000 Vac)
| UL AWM 1332 · 20 AWG | 300 Vac | 200 °C | 7/28 | 0.56 | 0.97 | 0.33 | 1.63 | 8 | 35.2 | UL 758 AWM · Style 1332 (300 Vac), Style 1330 (600 Vac) & Style 10203 (1,000 Vac)
| UL AWM 1332 · 16 AWG | 300 Vac | 200 °C | 19/29 | 1.23 | 1.5 | 0.33 | 2.16 | 15.5 | 15.8 | UL 758 AWM · Style 1332 (300 Vac), Style 1330 (600 Vac) & Style 10203 (1,000 Vac)
| UL AWM 1330 · 20 AWG | 600 Vac | 200 °C | 7/28 | 0.56 | 0.97 | 0.51 | 1.98 | 10.6 | 35.2 | UL 758 AWM · Style 1332 (300 Vac), Style 1330 (600 Vac) & Style 10203 (1,000 Vac)
| UL AWM 1330 · 16 AWG | 600 Vac | 200 °C | 19/29 | 1.23 | 1.5 | 0.51 | 2.51 | 18.8 | 15.8 | UL 758 AWM · Style 1332 (300 Vac), Style 1330 (600 Vac) & Style 10203 (1,000 Vac)
| UL AWM 1330 · 12 AWG | 600 Vac | 200 °C | 19/25 | 3.08 | 2.36 | 0.51 | 3.38 | 37.5 | 6.3 | UL 758 AWM · Style 1332 (300 Vac), Style 1330 (600 Vac) & Style 10203 (1,000 Vac)
| UL AWM 10203 · 10 AWG | 1,000 Vac | 200 °C | 37/26 | 4.74 | 2.95 | 0.51 | 3.96 | 55.2 | 4.1 | UL 758 AWM · Style 1332 (300 Vac), Style 1330 (600 Vac) & Style 10203 (1,000 Vac)
Additional gauges from 32 AWG up to 4/0 AWG and solid-conductor variants are manufactured to order across all six NEMA HP 4 and UL 758 style routes.

## Technical data
FEP High-Temperature Hook-Up Wire (NEMA HP 4 & UL 1330 / 1332 / 10203) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/fep-high-temperature-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ANSI/NEMA HP 4 & UL 758. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Max. operating T | +200 °C (UL 1330/1332/10203 & NEMA HP 4)
Key data | Voltage classes | 250–1,000 V (250 / 300 / 600 / 1,000 V)
Key data | Insulation | Extruded FEP (Melt-extruded FEP fluoropolymer)
Key data | AWG range | 32–4/0 AWG (32 AWG to 4/0 AWG)
Key data | Flammability | UL VW-1 / FT1 (Self-extinguishing fluoropolymer)
Key data | Min. bend radius | 6 × OD / 10 × OD (Fixed 6× · Flexing 10× OD)
Electrical | Rated voltage by style | 250 V RMS (NEMA HP 4 Type KT) · 300 Vac (UL 1332) · 600 V (NEMA HP 4 Type K & UL 1330) · 1,000 V (NEMA HP 4 Type KK & UL 10203)
Electrical | Dielectric constant & test voltage | Dielectric constant ~2.1 (1 kHz–1 GHz) · ≥ 1.5 kV (KT/1332), ≥ 2.0 kV (K/1330), ≥ 3.0 kV (KK/10203) AC dielectric test
Electrical | Conductor & plating options | Solid or concentric-stranded copper: tin-plated (up to 150 °C in NEMA HP 4; 200 °C in UL 1330/1332), silver-plated or nickel-plated (200 °C)
Thermal | Operating temperature range | −70 °C to +200 °C continuous (UL 1330, UL 1332, UL 10203 & silver/nickel NEMA HP 4; +150 °C for tin-plated NEMA HP 4)
Thermal | Continuous melt-extrusion advantage | Thermoplastic melt-extruded FEP enables long splice-free spool lengths up to +200 °C
Mechanical | Nominal FEP wall thickness by style | Type KT: 0.006 in (0.15 mm) thin wall · Type K: 0.010 in (0.25 mm) medium wall · Type KK: 0.015 in (0.38 mm) thick wall · UL 1332: 0.013 in (0.33 mm) · UL 1330 / 10203: 0.020 in (0.51 mm) heavy wall
Mechanical | Minimum bending radius | 6 × OD fixed; 10 × OD flexing
Resistance | Flame & chemical resistance | UL VW-1 vertical flame retardant; chemically inert to acids, alkalis, solvents, fuels, hydraulic oils and moisture
Resistance | Moisture & UV weatherability | Water absorption < 0.01%; immune to UV, ozone, fungi and outdoor weathering
Standards | Applicable standards | ANSI/NEMA HP 4-2021 (Types KT, K, KK; ex MIL-W-16878/11, /12, /13); UL 758 AWM Styles 1330, 1332, 10203
Standards | Environmental compliance | RoHS & REACH compliant fluoropolymer insulation system
Identification | Available NEMA & UL styles | 6 standard style routes: NEMA HP 4 Type KT (250 V), UL 1332 (300 V), NEMA HP 4 Type K (600 V), UL 1330 (600 V), NEMA HP 4 Type KK (1,000 V), UL 10203 (1,000 V)
Identification | Standard insulation colours | 10 standard solid colours (Black, White, Red, Blue, Yellow, Green, Brown, Orange, Violet, Grey) plus Green/Yellow

## Construction
FEP High-Temperature Hook-Up Wire (NEMA HP 4 & UL 1330 / 1332 / 10203) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/fep-high-temperature-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ANSI/NEMA HP 4 & UL 758. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Annealed copper conductor core | Solid or concentric-stranded high-conductivity annealed copper (32 AWG to 4/0 AWG) | ANSI/NEMA HP 4 & UL 758
2 | Tin, silver or nickel plating barrier | Electrolytic tin (150 °C), silver (200 °C) or nickel (200 °C) coating per ASTM B33 / B298 / B355 preventing copper oxidation | ANSI/NEMA HP 4-2021
3 | Extruded FEP insulation | Melt-extruded fluorinated ethylene propylene (FEP), 0.15 to 0.51 mm radial wall by voltage/style class | NEMA HP 4 / UL 758
| NEMA HP 4 Type KT / K / KK | 250 V thin-wall KT (32–20 AWG) · 600 V medium-wall K (32–8 AWG) · 1,000 V thick-wall KK (32–4/0 AWG) · 150 °C (tin) or 200 °C (silver/nickel)
| UL AWM Style 1332 (300 Vac) & Style 1330 (600 Vac) | 200 °C extruded FEP appliance wire: Style 1332 (0.33 mm wall, 30–10 AWG) and Style 1330 (0.51 mm wall, 30–4/0 AWG)
| UL AWM Style 10203 (1,000 Vac) | 1,000 Vac heavy-wall extruded FEP wire (30–4/0 AWG) for 150 °C or 200 °C internal equipment wiring

## Quality and supply
FEP High-Temperature Hook-Up Wire (NEMA HP 4 & UL 1330 / 1332 / 10203) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/fep-high-temperature-hook-up-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on ANSI/NEMA HP 4 & UL 758. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric & in-line spark test — 100% spark test and dielectric voltage withstand per NEMA HP 4 (1.5–3.0 kV) and UL 758 | Every spool
Routine test | Conductor DC resistance check — Verified at 20 °C per ASTM / NEMA HP 4 conductor class | Every spool
Sample test | UL VW-1 vertical flame test — Self-extinguishing fluoropolymer flame test per UL 758 / UL 1581 VW-1 | Production lot
Sample test | Thermal aging & concentricity check — 200 °C heat aging and FEP wall concentricity verification | Production lot
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · E-file UL AWM STYLE [1330 / 1332 / 10203] · [AWG] · 200°C · [300V / 600V / 1000V] · VW-1
Supply | Delivery form: Continuous splice-free spools, reels and barrel packs
Supply | Lengths: Standard spool lengths and custom cut-and-stripped leads
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None