## Request a quote
Request a quotation for FG16(O)R16
Share your required core count, cross-section (mm²), voltage class, armour/screen type, and drum lengths for FG16(O)R16.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/fg16-o-r16-ev-charging-station-dc-connection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
FG16(O)R16 EV Charging-Station DC Connection Cable – Dimensions & weights (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fg16-o-r16-ev-charging-station-dc-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI UNEL 35318 / CEI 20-13 / EN 50575 (FG16(O)R16 0.6/1 kV AC · 1.5 kV DC). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × Size | Main cross-section | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| FG16(O)R16 5G10 + 1×(2×1.5) mm² | 5G10 + (2×1.5) | 10.0 mm² | 21.4 | 525 | 760 | 107 | Standard FG16(O)R16 configurations
| FG16(O)R16 5G16 + 1×(2×1.5) mm² | 5G16 + (2×1.5) | 16.0 mm² | 24.2 | 815 | 1090 | 121 | Standard FG16(O)R16 configurations
| FG16(O)R16 3G35 + 1×(2×1.5) mm² DC Link | 3G35 + (2×1.5) | 35.0 mm² | 27.5 | 1060 | 1410 | 138 | Standard FG16(O)R16 configurations
| FG16(O)R16 3G50 + 1×(2×1.5) mm² DC Link | 3G50 + (2×1.5) | 50.0 mm² | 31.2 | 1510 | 1950 | 156 | Standard FG16(O)R16 configurations
| FG16(O)R16 3G70 + 1×(2×1.5) mm² DC Link | 3G70 + (2×1.5) | 70.0 mm² | 35.6 | 2090 | 2640 | 178 | Standard FG16(O)R16 configurations
| FG16(O)R16 2×95 + 1G50 + 1×(2×1.5) mm² HPC DC | 2×95 + 1G50 + (2×1.5) | 95.0 mm² | 37.8 | 2360 | 2980 | 189 | Standard FG16(O)R16 configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per CEI UNEL 35318 / CEI 20-13 / EN 50575 (FG16(O)R16 0.6/1 kV AC · 1.5 kV DC).

## Electrical & ampacity
FG16(O)R16 EV Charging-Station DC Connection Cable – Electrical & ampacity (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fg16-o-r16-ev-charging-station-dc-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI UNEL 35318 / CEI 20-13 / EN 50575 (FG16(O)R16 0.6/1 kV AC · 1.5 kV DC). Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Iz free air A | Iz tray / duct A | Isc (1 s) kA | Voltage drop mV/A/m | Dielectric test V
5G10 + (2×1.5) | 1.91 | 75 | 68 | 1.43 | 3.9 | 4000
5G16 + (2×1.5) | 1.21 | 100 | 90 | 2.29 | 2.5 | 4000
3G35 + (2×1.5) | 0.554 | 172 | 155 | 5.01 | 1.15 | 4000
3G50 + (2×1.5) | 0.386 | 210 | 189 | 7.15 | 0.8 | 4000
3G70 + (2×1.5) | 0.272 | 268 | 241 | 10.01 | 0.56 | 4000
2×95 + 1G50 + (2×1.5) | 0.206 | 328 | 295 | 13.59 | 0.42 | 4000
Conductor DC resistance at +20 °C per IEC 60228 and reference current ratings at 30 °C ambient per CEI UNEL 35318 / CEI 20-13 / EN 50575 (FG16(O)R16 0.6/1 kV AC · 1.5 kV DC).

## Technical data
FG16(O)R16 EV Charging-Station DC Connection Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/fg16-o-r16-ev-charging-station-dc-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI UNEL 35318 / CEI 20-13 / EN 50575 (FG16(O)R16 0.6/1 kV AC · 1.5 kV DC). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1kV / 1.5kV (0.6/1 kV AC · up to 1.5 kV DC)
Key data | Conductor | Class 5 Flex Cu (Flexible plain copper EN 60228)
Key data | Insulation | G16 HEPR 90 °C (High-modulus EPR rubber (+250°C Isc))
Key data | Pilot / data (O) | Cu-Screened Pair (C4/0.6/1 kV isolated control element)
Key data | Outer sheath | R16 Grey PVC (CPR Cca-s3,d1,a3 fire performance)
Key data | Min. bend radius | 4 × D / 6 × D (Flexible Class 5 cabinet & duct routing)
Electrical | Rated voltage U0/U (AC / DC) | 0.6/1 kV AC · up to 1.5 kV DC (1,800 V DC
Electrical | Pilot unit rated voltage | 0.6/1 kV (co-rated for safe co-existence
Electrical | AC dielectric test voltage | 4,000 V AC for 5 minutes
Electrical | Max. conductor operating temp. | +90 °C continuous · +250 °C short-circuit
Electrical | Current rating advantage | +15 % higher ampacity than 70 °C PVC cables
Thermal | Operating ambient temperature | -30 °C to +80 °C (max. conductor +90 °C)
Thermal | Minimum installation temp. | -15 °C
Mechanical | Min. bending radius | 4 × D (D ≤ 25 mm) · 5 × D (D > 25 mm) fixed
Mechanical | Impact & water immersion | AG2 medium impact · AD8 permanent water
Resistance | CPR fire reaction class | EN 50575 Class Cca-s3,d1,a3 (EN 50399 / EN
Resistance | Low smoke & oil resistance | EN 61034-2 · CEI 20-34 hydrocarbon &
Standards | Primary specification | CEI UNEL 35318 · CEI 20-13 · EN 50575
Standards | Italian fire code compliance | IMQ EFP certified for public garages &
Identification | Core colours | DC: Red/Black or Brown/Blue + G/Y · Pilot
Identification | Outer sheath colour | RAL 7001 Grey

## Construction
FG16(O)R16 EV Charging-Station DC Connection Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/fg16-o-r16-ev-charging-station-dc-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI UNEL 35318 / CEI 20-13 / EN 50575 (FG16(O)R16 0.6/1 kV AC · 1.5 kV DC). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 flexible copper power & pilot | EN 60228 Class 5 flexible annealed copper power cores (16–150 mm²) + Class 5 pilot cores | CEI EN 60228
2 | G16 HEPR rubber insulation (90 °C) | High-modulus cross-linked ethylene-propylene elastomer (G16 per CEI 20-11) on power and | CEI 20-13 / UNEL 35318
3 | Individual copper screen '(O)' on | Tinned copper wire braid (≥ 85 % coverage) + polyester wrap isolating the control/pilot | CEI UNEL 35318 (O)
4 | Inner filler / bedding | Flame-retardant elastomeric filler maintaining circular cross-section | CEI 20-13
5 | R16 outer sheath (CPR Cca) | Special abrasion- and hydrocarbon-resistant PVC compound Type R16 (RAL 7001 Grey) | CEI 20-11 / EN 50575 Cca
| FG16(O)R16 DC Dispenser Link (2×35–2×150 + 1G + (2×1.5)) | DC+/DC- power cores + protective earth + copper-screened pilot pair for 50–350 kW DC satellite dispensers.
| FG16(O)R16 3-Phase AC/DC Hybrid (5G6–5G50 + (2×1.5)) | 5 power cores + screened control pair for smart AC/DC chargers with remote emergency-stop and CAN/RS-485 link.

## Quality and supply
FG16(O)R16 EV Charging-Station DC Connection Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/fg16-o-r16-ev-charging-station-dc-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on CEI UNEL 35318 / CEI 20-13 / EN 50575 (FG16(O)R16 0.6/1 kV AC · 1.5 kV DC). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 4.0 kV AC dielectric test on power & pilot cores — 4,000 V AC for 5 min per CEI 20-13 without breakdown | 100 % of drums
Routine test | Class 5 DC conductor resistance @ 20 °C — CEI EN 60228 Class 5 flexible copper limits | 100 % of drums
Sample test | G16 HEPR elastic modulus & hot-set test — CEI 20-11 G16 high-modulus cross-linking verification | Per production batch
Type test | EN 50399 CPR Cca-s3,d1,a3 fire & smoke test — Heat release, flame spread & droplet compliance | Notified body DoP
Standard / approval | CEI UNEL 35318 / CEI 20-13
Standard / approval | EN 50575 CPR Cca-s3,d1,a3
Standard / approval | AD8 Submersion Rated
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX FG16(O)R16-0.6/1KV CEI UNEL 35318
Supply | Delivery form: Non-returnable timber drums or heavy export
Supply | Standard drum lengths: 250 m · 500 m · 1000 m · custom cut lengths
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP