## Request a quote
Request a quotation for FOUNDATION Fieldbus H1
Share your protocol/frequency, jacket material (PVC, PUR, LSZH, FEP), and installation motion for FOUNDATION Fieldbus H1.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/foundation-fieldbus-h1-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
FOUNDATION Fieldbus H1 Cable – Dimensions & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/foundation-fieldbus-h1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A / ISA SP50.02 (FOUNDATION Fieldbus H1). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Conductor size | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| FF H1 Type A 1×2×18 AWG Unarmoured Orange | 1×2×18 AWG (Single-Pair Trunk) | 18 AWG (0.88 mm²) | 7.6 | 32 | 72 | 61 | Standard FOUNDATION Fieldbus H1 configurations
| FF H1 Type A 1×2×16 AWG Heavy Trunk Orange | 1×2×16 AWG (Long-Reach Trunk) | 16 AWG (1.31 mm²) | 8.6 | 44 | 94 | 69 | Standard FOUNDATION Fieldbus H1 configurations
| FF H1 Type A 1×2×18 AWG SWA Armoured | 1×2×18 AWG (SWA Armoured) | 18 AWG (0.88 mm²) | 12.2 | 32 | 240 | 98 | Standard FOUNDATION Fieldbus H1 configurations
| FF H1 Multi-Pair Homerun 4×2×18 AWG IS/OS | 4×2×18 AWG (4-Pair Homerun) | 18 AWG (0.88 mm²) | 14.8 | 118 | 235 | 118 | Standard FOUNDATION Fieldbus H1 configurations
| FF H1 Multi-Pair Homerun 8×2×18 AWG IS/OS | 8×2×18 AWG (8-Pair Homerun) | 18 AWG (0.88 mm²) | 19.5 | 232 | 410 | 156 | Standard FOUNDATION Fieldbus H1 configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per IEC 61158-2 Type A / ISA SP50.02 (FOUNDATION Fieldbus H1).

## Impedance, capacitance & attenu
FOUNDATION Fieldbus H1 Cable – Impedance, capacitance & attenuation (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/foundation-fieldbus-h1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A / ISA SP50.02 (FOUNDATION Fieldbus H1). Values for your order are confirmed in the quotation.
Configuration | Impedance Z0 | Max. DC R @ 20 °C Ω/km | Mutual C pF/m ≈ | VoP % | Attenuation @ 20 °C dB/100m | Dielectric test V
1×2×18 AWG (Single-Pair Trunk) | 100 Ω | 44 | 48 | 67 | 0.28 dB/100m @ 39 kHz | 1500
1×2×16 AWG (Long-Reach Trunk) | 100 Ω | 28 | 50 | 67 | 0.22 dB/100m @ 39 kHz | 1500
1×2×18 AWG (SWA Armoured) | 100 Ω | 44 | 48 | 67 | 0.28 dB/100m @ 39 kHz | 1500
4×2×18 AWG (4-Pair Homerun) | 100 Ω | 44 | 48 | 67 | 0.28 dB/100m @ 39 kHz | 1500
8×2×18 AWG (8-Pair Homerun) | 100 Ω | 44 | 48 | 67 | 0.28 dB/100m @ 39 kHz | 1500
Transmission values (characteristic impedance Z0, mutual capacitance, VoP, and attenuation) are measured at +20 °C per IEC 61158-2 Type A / ISA SP50.02 (FOUNDATION Fieldbus H1).

## Technical data
FOUNDATION Fieldbus H1 Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/foundation-fieldbus-h1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A / ISA SP50.02 (FOUNDATION Fieldbus H1). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Impedance Z0 | 100 Ω ± 20 Ω (At 31.25 kHz Manchester MBP)
Key data | Pair counts | 1P to 12P × 18 (Single-pair & multi-pair homerun)
Key data | Loop resistance | ≤ 44 Ω / km (18 AWG (0.8 mm²) · ≤ 28 Ω/km (16 AWG))
Key data | Attenuation | ≤ 3.0 dB / km (At 39 kHz (≤ 0.30 dB/100m))
Key data | Max. segment | 1,900 m (Non-Ex 1900 m · FISCO Ex-ia 1000 m)
Key data | Sheath & armour | PVC / LSZH / SWA (Orange (Non-Ex), Blue (Ex-i), SWA)
Electrical | Characteristic impedance Z0 | 100 Ω ± 20 Ω at 31.25 kHz
Electrical | Max. DC loop resistance @ 20 °C | ≤ 44 Ω/km (18 AWG) · ≤ 28 Ω/km (16 AWG)
Electrical | Mutual capacitance @ 1 kHz | ≈ 48 pF/m (standard limit ≤ 60 nF/km)
Electrical | Attenuation @ 39 kHz | ≤ 3.0 dB/km (≤ 0.30 dB/100m)
Electrical | Max. propagation delay | ≤ 1.7 µs/km (VoP ≈ 66–68 %)
Electrical | Operating / test voltage | 300 V (UL PLTC / ITC) · 1.5 kV AC
Thermal | Operating temp. (fixed) | -40 °C to +105 °C (105 °C PLTC PVC) · -40
Thermal | Installation temperature | -20 °C to +60 °C
Mechanical | Min. bending radius | 8 × D unarmoured · 12 × D SWA armoured
Mechanical | Crush & impact resistance | UL 13 PLTC / EN 50288-7 industrial tray
Resistance | Sunlight, oil & chemical resistance | UL Sunlight Resistant · Oil Res I/II · EN
Resistance | Flame retardancy | IEC 60332-3-24 Cat C / UL 1685 FT4 Vertical
Standards | Primary specification | IEC 61158-2 Type A · ISA SP50.02 ·
Standards | Hazardous location ratings | NEC Class I Div 2 (PLTC-ER) · ATEX/IECEx
Identification | Core polarity colours | Orange (+) & Blue (-) — numbered pairs on
Identification | Outer sheath colour | Orange (standard Non-Ex), Yellow, or Blue

## Construction
FOUNDATION Fieldbus H1 Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/foundation-fieldbus-h1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A / ISA SP50.02 (FOUNDATION Fieldbus H1). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Stranded tinned copper conductors | 18 AWG (7×0.40 mm, 0.88 mm²) or 16 AWG (7×0.49 mm, 1.31 mm²) tinned copper | IEC 61158-2 / ISA SP50.02
2 | Polyolefin / PE dielectric | Low-capacitance polyethylene or foam-skin PE tuned to Z0 = 100 Ω @ 31.25 kHz | IEC 61158-2 Type A
3 | Pair & collective Al/PET screen | 100 % coverage Al/PET tape with 20 AWG tinned copper drain wire (PiMF + overall screen | ISA SP50.02 Type A
4 | Optional tinned Cu braid or SWA armour | Tinned copper braid (≥80 %) or galvanized steel wire armour (SWA) for mechanical | EN 50288-7 / BS 5308
5 | Outer sheath | Flame-retardant PVC, LSZH (SHF1), or PUR in RAL 2003 Orange, Yellow, or RAL 5015 Ex-i Blue | UL 13 PLTC / IEC 60332-3-24
| FF H1 Single-Pair Spur/Trunk (1×2×18 AWG & 16 AWG) | Standard Orange, Yellow, or Ex-i Blue single-pair Type A cable (unarmoured or SWA armoured).
| FF H1 Multi-Pair Homerun (2P, 4P, 8P, 12P × 18 AWG) | Individually and overall screened (IS/OS) multi-pair trunk cable connecting field junction boxes to DCS

## Quality and supply
FOUNDATION Fieldbus H1 Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/foundation-fieldbus-h1-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 61158-2 Type A / ISA SP50.02 (FOUNDATION Fieldbus H1). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 31.25 kHz impedance Z0 & 39 kHz attenuation — Z0 = 100 ± 20 Ω; attenuation ≤ 3.0 dB/km | 100 % of reels
Routine test | DC loop resistance, capacitance & 1.5 kV AC — ≤ 44 Ω/km (18 AWG); ≤ 60 nF/km; 1.5 kV AC dielectric | 100 % of reels
Sample test | Pair-to-pair crosstalk (Multi-pair IS/OS homerun) — ≥ 60 dB at 39 kHz between individually shielded pairs | Per production batch
Type test | IEC 60332-3-24 Cat C / UL 1685 FT4 tray flame — Vertical tray flame propagation pass | Type approval
Standard / approval | IEC 61158-2 / ISA SP50.02
Standard / approval | FieldComm Group FF-844
Standard / approval | UL 13 PLTC / ITC FT4
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX FOUNDATION FIELDBUS H1 TYPE A
Supply | Delivery form: Non-returnable plywood reels or export drums
Supply | Standard reel lengths: 100 m · 305 m · 500 m · 1000 m
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP