## Request a quote
Request a quotation for FPLP
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/fplp-plenum-fire-alarm-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
FPLP Plenum Fire Alarm Cable – Dimensions & masses (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplp-plenum-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / NFPA 70 (NEC Art. 760). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | AWG & Cores | Area mm² | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| FPLP 18/2 Unshielded | 2C × 18 AWG | 0.82 mm² | 3.9 | 16 | 26 | 31 | FPLP standard series
| FPLP 18/4 Unshielded | 4C × 18 AWG | 0.82 mm² | 4.6 | 31 | 45 | 37 | FPLP standard series
| FPLP 16/2 Unshielded | 2C × 16 AWG | 1.31 mm² | 4.5 | 25 | 38 | 36 | FPLP standard series
| FPLP 16/4 Unshielded | 4C × 16 AWG | 1.31 mm² | 5.3 | 50 | 66 | 42 | FPLP standard series
| FPLP 14/2 Unshielded | 2C × 14 AWG | 2.08 mm² | 5.4 | 40 | 56 | 43 | FPLP standard series
| FPLP 14/4 Unshielded | 4C × 14 AWG | 2.08 mm² | 6.4 | 79 | 102 | 51 | FPLP standard series
| FPLP 12/2 Unshielded | 2C × 12 AWG | 3.31 mm² | 6.3 | 63 | 84 | 50 | FPLP standard series
| FPLP 18/2 Shielded OAS | 2C × 18 AWG OAS | 0.82 mm² | 4.1 | 19 | 30 | 33 | FPLP standard series
| FPLP 18/4 Shielded OAS | 4C × 18 AWG OAS | 0.82 mm² | 4.8 | 35 | 49 | 38 | FPLP standard series
| FPLP 16/2 Shielded OAS | 2C × 16 AWG OAS | 1.31 mm² | 4.7 | 28 | 42 | 38 | FPLP standard series
| FPLP 16/4 Shielded OAS | 4C × 16 AWG OAS | 1.31 mm² | 5.5 | 53 | 71 | 44 | FPLP standard series
| FPLP 14/2 Shielded OAS | 2C × 14 AWG OAS | 2.08 mm² | 5.6 | 43 | 61 | 45 | FPLP standard series
| FPLP 12/2 Shielded OAS | 2C × 12 AWG OAS | 3.31 mm² | 6.5 | 67 | 90 | 52 | FPLP standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per UL 1424 / NFPA 70 (NEC Art. 760).

## Electrical data
FPLP Plenum Fire Alarm Cable – Electrical data (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplp-plenum-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / NFPA 70 (NEC Art. 760). Values for your order are confirmed in the quotation.
AWG & Cores | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
2C × 18 AWG | 21.4 | 7 | 6
4C × 18 AWG | 21.4 | 6 | 5
2C × 16 AWG | 13.5 | 10 | 9
4C × 16 AWG | 13.5 | 8 | 7
2C × 14 AWG | 8.45 | 15 | 13
4C × 14 AWG | 8.45 | 12 | 10
2C × 12 AWG | 5.31 | 20 | 17
2C × 18 AWG OAS | 21.4 | 7 | 6
4C × 18 AWG OAS | 21.4 | 6 | 5
2C × 16 AWG OAS | 13.5 | 10 | 9
4C × 16 AWG OAS | 13.5 | 8 | 7
2C × 14 AWG OAS | 8.45 | 15 | 13
2C × 12 AWG OAS | 5.31 | 20 | 17
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
FPLP Plenum Fire Alarm Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplp-plenum-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / NFPA 70 (NEC Art. 760). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 300 V (Power-limited fire alarm (NEC 760))
Key data | Flame & smoke | NFPA 262 (UL 910 (Flame ≤5 ft · peak optical smoke ≤0.50)
Key data | Conductor range | 18 to 12 AWG (Solid bare annealed copper)
Key data | Insulation | FEP / Low-Smoke (Fluoropolymer or low-smoke compound)
Key data | Operating temp | 0 to +75 °C (Up to +150 °C on FEP plenum grades)
Key data | Min. bend radius | 8 × cable OD (Plenum ceiling & J-hook routing)
Electrical | NEC / UL voltage rating | 300 V rms (power-limited fire alarm)
Electrical | Dielectric withstand test | 1500 V AC for 1 minute
Electrical | Nominal capacitance (18 AWG) | ≈82 pF/m unshielded · ≈145 pF/m shielded
Thermal | UL temperature rating | 75 °C (low-smoke alloy) / 150 °C (FEP)
Thermal | Operating temperature range | 0 °C to +75 °C (up to +150 °C FEP)
Mechanical | Min. installation bend radius | 8 × cable OD (unshielded) · 10 × OD (shielded)
Mechanical | Ripcord | Integral high-tensile nylon ripcord under jacket
Resistance | Steiner Tunnel plenum test | NFPA 262 / UL 910 (flame travel ≤1.52 m, peak optical smoke ≤0.50, avg ≤0.15)
Resistance | Substitution hierarchy | Permitted to substitute for FPLR, FPL, CMP, CMR, CL3P, CL2P per NEC 760.154
Standards | Safety & listing standard | UL 1424 Type FPLP
Standards | Installation code | NFPA 70 (NEC Article 760) & NFPA 72
Identification | Conductor colour code | 2C: Black, Red · 4C: Black, Red, Brown, Blue (or Green/Yellow)
Identification | Jacket colour | Fire Alarm Red

## Construction
FPLP Plenum Fire Alarm Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplp-plenum-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / NFPA 70 (NEC Art. 760). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper conductor | Solid annealed uncoated copper (18, 16, 14 or 12 AWG) per ASTM B3 | ASTM B3
2 | Plenum low-smoke insulation | Fluorinated ethylene propylene (FEP) or low-smoke flame-retardant plenum compound | UL 1424
3 | Foil shield + drain (shielded types) | 100 % coverage aluminum/polyester tape with 20–24 AWG stranded tinned copper drain wire | UL 1424
4 | Low-smoke plenum jacket | NFPA 262 compliant low-smoke flame-retardant PVDF or LS-PVC jacket with nylon ripcord, Fire Alarm Red | UL 1424
| FPLP Unshielded | 2C and 4C unshielded cabled or twisted pairs for NAC horn/strobe circuits and conventional detection.
| FPLP Overall Foil Shielded (OAS) | 100 % Al-Mylar foil shield + tinned copper drain wire for addressable SLC data loops and 25/70 Vrms voice evac.

## Quality and supply
FPLP Plenum Fire Alarm Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplp-plenum-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / NFPA 70 (NEC Art. 760). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1500 V AC dielectric test & spark test — Zero insulation breakdown per UL 1424 | 100 % of reels
Routine test | DC conductor resistance & continuity — Meets ASTM B3 solid copper limits at 20 °C | 100 % of reels
Type test | NFPA 262 (UL 910) Steiner Tunnel plenum test — Max flame spread ≤5.0 ft (1.52 m), peak optical smoke density ≤0.50, average ≤0.15 | UL Type FPLP listing
Standard / approval | UL 1424 Type FPLP
Standard / approval | NFPA 262 (UL 910) Plenum
Standard / approval | NFPA 70 (NEC Article 760)
Standard / approval | NFPA 72 National Fire Alarm Code
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX E-FILE 16 AWG 2C SHIELDED (UL) TYPE FPLP OR CL3P 75C SUN RES NFPA 262 [foot/meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP