## Request a quote
Request a quotation for FPLR
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/fplr-riser-fire-alarm-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
FPLR Riser Fire Alarm Cable – Dimensions & masses (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplr-riser-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / UL 1666 (NEC Art. 760). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | AWG & Cores | Area mm² | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| FPLR 18/2 Unshielded | 2C × 18 AWG | 0.82 mm² | 3.8 | 16 | 25 | 30 | FPLR standard series
| FPLR 18/4 Unshielded | 4C × 18 AWG | 0.82 mm² | 4.5 | 31 | 43 | 36 | FPLR standard series
| FPLR 16/2 Unshielded | 2C × 16 AWG | 1.31 mm² | 4.4 | 25 | 36 | 35 | FPLR standard series
| FPLR 16/4 Unshielded | 4C × 16 AWG | 1.31 mm² | 5.2 | 50 | 63 | 42 | FPLR standard series
| FPLR 14/2 Unshielded | 2C × 14 AWG | 2.08 mm² | 5.3 | 40 | 54 | 42 | FPLR standard series
| FPLR 14/4 Unshielded | 4C × 14 AWG | 2.08 mm² | 6.3 | 79 | 98 | 50 | FPLR standard series
| FPLR 12/2 Unshielded | 2C × 12 AWG | 3.31 mm² | 6.2 | 63 | 81 | 50 | FPLR standard series
| FPLR 18/2 Shielded OAS | 2C × 18 AWG OAS | 0.82 mm² | 4 | 19 | 28 | 32 | FPLR standard series
| FPLR 18/4 Shielded OAS | 4C × 18 AWG OAS | 0.82 mm² | 4.7 | 35 | 47 | 38 | FPLR standard series
| FPLR 16/2 Shielded OAS | 2C × 16 AWG OAS | 1.31 mm² | 4.6 | 28 | 40 | 37 | FPLR standard series
| FPLR 16/4 Shielded OAS | 4C × 16 AWG OAS | 1.31 mm² | 5.4 | 53 | 68 | 43 | FPLR standard series
| FPLR 14/2 Shielded OAS | 2C × 14 AWG OAS | 2.08 mm² | 5.5 | 43 | 59 | 44 | FPLR standard series
| FPLR 12/2 Shielded OAS | 2C × 12 AWG OAS | 3.31 mm² | 6.4 | 67 | 87 | 51 | FPLR standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per UL 1424 / UL 1666 (NEC Art. 760).

## Electrical data
FPLR Riser Fire Alarm Cable – Electrical data (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplr-riser-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / UL 1666 (NEC Art. 760). Values for your order are confirmed in the quotation.
AWG & Cores | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
2C × 18 AWG | 21.4 | 7 | 6
4C × 18 AWG | 21.4 | 6 | 5
2C × 16 AWG | 13.5 | 10 | 9
4C × 16 AWG | 13.5 | 8 | 7
2C × 14 AWG | 8.45 | 15 | 13
4C × 14 AWG | 8.45 | 12 | 10
2C × 12 AWG | 5.31 | 20 | 17
2C × 18 AWG OAS | 21.4 | 7 | 6
4C × 18 AWG OAS | 21.4 | 6 | 5
2C × 16 AWG OAS | 13.5 | 10 | 9
4C × 16 AWG OAS | 13.5 | 8 | 7
2C × 14 AWG OAS | 8.45 | 15 | 13
2C × 12 AWG OAS | 5.31 | 20 | 17
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
FPLR Riser Fire Alarm Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplr-riser-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / UL 1666 (NEC Art. 760). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 300 V (Power-limited fire alarm (NEC 760))
Key data | Riser flame test | UL 1666 (Vertical shaft flame height <12 ft)
Key data | Conductor range | 18 to 12 AWG (Solid bare annealed copper)
Key data | Insulation | FR-PVC / PP (Flame-retardant PVC or polypropylene)
Key data | Operating temp | -20 to +75 °C (UL 75 °C temperature rating)
Key data | Min. bend radius | 8 × cable OD (Vertical shaft & conduit pulling)
Electrical | NEC / UL voltage rating | 300 V rms (power-limited fire alarm)
Electrical | Dielectric withstand test | 1500 V AC for 1 minute
Electrical | Nominal capacitance (18 AWG) | ≈75 pF/m unshielded · ≈138 pF/m shielded
Thermal | UL temperature rating | 75 °C
Thermal | Operating temperature range | -20 °C to +75 °C
Mechanical | Min. installation bend radius | 8 × cable OD
Mechanical | Ripcord | Integral nylon ripcord for fast jacket stripping
Resistance | Vertical riser shaft flame test | UL 1666 (145 kW propane burner, flame propagation <12 ft / 3.66 m, temp <454.4 °C at 12 ft)
Resistance | Substitution hierarchy | Replaces Type FPL, CMR, CL3R and CL2R per NEC 760.154(B)
Standards | Safety standard | UL 1424 Type FPLR & UL 1666
Standards | Installation code | NFPA 70 (NEC Article 760) & NFPA 72
Identification | Conductor colour code | 2C: Black, Red · 4C: Black, Red, Brown, Blue
Identification | Jacket colour | Fire Alarm Red

## Construction
FPLR Riser Fire Alarm Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplr-riser-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / UL 1666 (NEC Art. 760). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper conductor | Solid annealed uncoated copper (18, 16, 14 or 12 AWG) per ASTM B3 | ASTM B3
2 | Flame-retardant riser insulation | Colour-coded flame-retardant PVC or low-capacitance polypropylene compound | UL 1424
3 | Al-Mylar shield + drain (shielded) | 100 % coverage aluminum/polyester tape with stranded tinned copper drain wire | UL 1424
4 | UL 1666 riser outer jacket | Flame-retardant riser-grade PVC outer jacket with integral ripcord, Fire Alarm Red | UL 1666
| FPLR Unshielded | 2C and 4C unshielded riser cable for Notification Appliance Circuits (NAC), horn/strobes and conventional zones.
| FPLR Overall Foil Shielded (OAS) | 100 % Al-Mylar tape + tinned Cu drain wire for EMI-protected SLC addressable loops and voice evac speakers.

## Quality and supply
FPLR Riser Fire Alarm Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/fplr-riser-fire-alarm-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on UL 1424 / UL 1666 (NEC Art. 760). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 1500 V AC dielectric test & spark test — Zero insulation breakdown per UL 1424 | 100 % of reels
Routine test | DC conductor resistance check — Conforms to ASTM B3 at 20 °C | 100 % of reels
Type test | UL 1666 vertical riser shaft flame test — Flame propagation height <12 ft (3.66 m) and temperature <850 °F (454.4 °C) at 12 ft | UL Type FPLR listing
Standard / approval | UL 1424 Type FPLR
Standard / approval | UL 1666 Vertical Riser
Standard / approval | NFPA 70 (NEC Article 760)
Standard / approval | NFPA 72 National Fire Alarm Code
Standard / approval | RoHS 3 Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX E-FILE 14 AWG 2C (UL) TYPE FPLR OR CL3R 75C UL 1666 FIRE ALARM CABLE [foot/meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP