## Request a quote
Request a quotation for Fire-Resistant FO FE180
Specify circuit-integrity rating, core count, conductor cross-section and required drum lengths.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/hitronic-fire-circuit-integrity-fire-resistant-fibre-optic-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Fire-Resistant FO FE180 Circuit-Integrity Fibre Optic Cable – Dimensions & masses (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/hitronic-fire-circuit-integrity-fire-resistant-fibre-optic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60331-25 / DIN 4102-12. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Fibres & Mode | Core/Clad µm | Outer Ø ≈ mm | Copper kg/km | Total weight ≈ kg/km | Min. bend R fixed mm | Series
| HITRONIC FIRE 4G50/125 OM3 FE180/E90 | 4F OM3 Multimode | 50/125 µm | 10.2 | 0 | 135 | 153 | HITRONIC FIRE standard series
| HITRONIC FIRE 8G50/125 OM3 FE180/E90 | 8F OM3 Multimode | 50/125 µm | 10.2 | 0 | 136 | 153 | HITRONIC FIRE standard series
| HITRONIC FIRE 12G50/125 OM3 FE180/E90 | 12F OM3 Multimode | 50/125 µm | 10.5 | 0 | 142 | 158 | HITRONIC FIRE standard series
| HITRONIC FIRE 24G50/125 OM3 FE180/E90 | 24F OM3 Multimode | 50/125 µm | 11.4 | 0 | 168 | 171 | HITRONIC FIRE standard series
| HITRONIC FIRE 4G50/125 OM4 FE180/E90 | 4F OM4 Multimode | 50/125 µm | 10.2 | 0 | 135 | 153 | HITRONIC FIRE standard series
| HITRONIC FIRE 8G50/125 OM4 FE180/E90 | 8F OM4 Multimode | 50/125 µm | 10.2 | 0 | 136 | 153 | HITRONIC FIRE standard series
| HITRONIC FIRE 12G50/125 OM4 FE180/E90 | 12F OM4 Multimode | 50/125 µm | 10.5 | 0 | 142 | 158 | HITRONIC FIRE standard series
| HITRONIC FIRE 24G50/125 OM4 FE180/E90 | 24F OM4 Multimode | 50/125 µm | 11.4 | 0 | 168 | 171 | HITRONIC FIRE standard series
| HITRONIC FIRE 4E9/125 OS2 FE180/E90 | 4F OS2 Single-Mode | 9/125 µm | 10.2 | 0 | 135 | 153 | HITRONIC FIRE standard series
| HITRONIC FIRE 8E9/125 OS2 FE180/E90 | 8F OS2 Single-Mode | 9/125 µm | 10.2 | 0 | 136 | 153 | HITRONIC FIRE standard series
| HITRONIC FIRE 12E9/125 OS2 FE180/E90 | 12F OS2 Single-Mode | 9/125 µm | 10.5 | 0 | 142 | 158 | HITRONIC FIRE standard series
| HITRONIC FIRE 24E9/125 OS2 FE180/E90 | 24F OS2 Single-Mode | 9/125 µm | 11.4 | 0 | 168 | 171 | HITRONIC FIRE standard series
| HITRONIC FIRE 48E9/125 OS2 FE180/E90 | 48F OS2 Single-Mode | 9/125 µm | 13.8 | 0 | 235 | 207 | HITRONIC FIRE standard series
Nominal outer diameters and weights are subject to manufacturing tolerances per IEC 60331-25 / DIN 4102-12.

## Electrical data
Fire-Resistant FO FE180 Circuit-Integrity Fibre Optic Cable – Electrical data (13)
TEBAOFLEX ¦ https://tebaoflex.com/cables/hitronic-fire-circuit-integrity-fire-resistant-fibre-optic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60331-25 / DIN 4102-12. Values for your order are confirmed in the quotation.
Fibres & Mode | Max. DC R @ 20 °C Ω/km | Current in air A | Current in duct/tray A
4F OM3 Multimode | 0.35 | 2000 | 1720
8F OM3 Multimode | 0.35 | 2000 | 1720
12F OM3 Multimode | 0.35 | 2000 | 1720
24F OM3 Multimode | 0.35 | 2000 | 1720
4F OM4 Multimode | 0.35 | 2000 | 1720
8F OM4 Multimode | 0.35 | 2000 | 1720
12F OM4 Multimode | 0.35 | 2000 | 1720
24F OM4 Multimode | 0.35 | 2000 | 1720
4F OS2 Single-Mode | 0.22 | 2000 | 1720
8F OS2 Single-Mode | 0.22 | 2000 | 1720
12F OS2 Single-Mode | 0.22 | 2000 | 1720
24F OS2 Single-Mode | 0.22 | 2000 | 1720
48F OS2 Single-Mode | 0.22 | 2500 | 2150
Current ratings apply at +30 °C ambient in free air and +25 °C in enclosed tray/conduit.

## Technical data
Fire-Resistant FO FE180 Circuit-Integrity Fibre Optic Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/hitronic-fire-circuit-integrity-fire-resistant-fibre-optic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60331-25 / DIN 4102-12. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Fibre counts | 4 to 48 fibres (Central or stranded metal/gel tube)
Key data | Fire integrity | FE180 E30–E90 (180 min @ ≥750 °C (IEC 60331-25))
Key data | Fibre grades | OS2 / OM3 / OM4 (ITU-T G.652.D / G.657.A1 & ISO 11801)
Key data | Armouring | Corrugated steel (Longitudinal CST + glass roving)
Key data | Operating temp | -30 to +70 °C (Indoor/outdoor tunnel & riser)
Key data | Min. bend radius | 15×D / 20×D (15×OD static · 20×OD dynamic pull)
Electrical | Dielectric / metallic classification | Metal-armoured optical cable (CST armour requires equipotential earthing at entry)
Electrical | Max. attenuation increase in fire | ≤0.5 dB/km (or link budget continuity) during 180 min @ 750 °C
Thermal | Operating temperature range | -30 °C to +70 °C
Thermal | Installation temperature range | -10 °C to +50 °C
Thermal | Fire endurance temperature | ≥750 °C (IEC 60331-25) / up to 1000 °C (DIN 4102-12 E30–E90)
Mechanical | Min. bend radius (static / dynamic) | 15 × cable OD (fixed) · 20 × cable OD (during pulling)
Mechanical | Max. tensile pulling load | 2000 N (short-term installation) · 1000 N (permanent)
Mechanical | Crush resistance | ≥3000 N/100 mm per IEC 60794-1-21 Method E3
Optical | Attenuation OS2 @ 1310 / 1550 nm | ≤0.36 dB/km @ 1310 nm · ≤0.22 dB/km @ 1550 nm
Optical | Attenuation OM3 / OM4 @ 850 / 1300 nm | ≤2.5 dB/km @ 850 nm · ≤0.7 dB/km @ 1300 nm
Optical | Bandwidth OM3 / OM4 @ 850 nm | OM3 ≥2000 MHz·km · OM4 ≥4700 MHz·km (EMB)
Resistance | Optical circuit integrity in fire | FE180 (180 min @ ≥750 °C + 15 min cool-down per IEC 60331-25)
Resistance | System functional integrity | E30 / E60 / E90 per DIN 4102-12
Resistance | Flame, smoke & halogen | IEC 60332-3-24 Cat. C, IEC 61034-2 (≥60 %), IEC 60754-2 (pH ≥4.3)
Standards | Fire test standard | IEC 60331-25 & DIN 4102-12
Standards | Optical cable standard | IEC 60794-1-21 / IEC 60794-1-22 & ISO/IEC 11801
Identification | Fibre colour code | IEC 60304 / DIN VDE 0888 12-colour sequence
Identification | Outer sheath colour | Orange (RAL 2003), Red (RAL 3000) or Black

## Construction
Fire-Resistant FO FE180 Circuit-Integrity Fibre Optic Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/hitronic-fire-circuit-integrity-fire-resistant-fibre-optic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60331-25 / DIN 4102-12. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Optical glass fibres (OS2 / OM3 / OM4) | 4 to 48 colour-coded 250 µm acrylate-coated silica optical fibres per IEC 60793-2-50 / -10 | IEC 60793-2
2 | Metallic / fire-resistant central loose tube | Thixotropic gel-filled stainless-steel or mica-wrapped composite loose buffer tube protecting fibres from thermal crush | IEC 60794-1
3 | Glass-roving & mica thermal barrier | High-density E-glass roving yarns and phlogopite mica flame barrier tape providing tensile strength and thermal insulation | IEC 60331-25
4 | Corrugated steel tape armour (CST) | Longitudinally formed and overlapped corrugated steel tape providing crush, impact and 100 % rodent protection | IEC 60794-1
5 | LSZH fire-safety outer sheath | Halogen-free, low-smoke flame-retardant thermoplastic compound (Orange, Red or Black) | IEC 60332-3-24
| HITRONIC FIRE OS2 (9/125 µm Single-Mode) | ITU-T G.652.D / G.657.A1 single-mode fibres for multi-kilometre tunnel SCADA, railway signalling and campus fire rings.
| HITRONIC FIRE OM3 / OM4 (50/125 µm Multimode) | Laser-optimised 50/125 µm multimode fibres for high-speed building risers, hospital backbones and PA/VA networks.

## Quality and supply
Fire-Resistant FO FE180 Circuit-Integrity Fibre Optic Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/hitronic-fire-circuit-integrity-fire-resistant-fibre-optic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60331-25 / DIN 4102-12. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % OTDR optical attenuation & continuity trace — Attenuation ≤0.36/0.22 dB/km (OS2) or ≤2.5/0.7 dB/km (OM3/OM4) with zero point defects | 100 % of fibres on every drum
Type test | IEC 60331-25 optical circuit integrity under fire (FE180) — 180 minutes at ≥750 °C flame + 15 min cooling with optical attenuation increase within limit | Type qualification
Type test | DIN 4102-12 furnace functional endurance (E30–E90) — 30 to 90 minutes optical transmission survival up to 1000 °C on tested tray systems | Type qualification
Standard / approval | IEC 60331-25 FE180
Standard / approval | DIN 4102-12 E30 / E60 / E90
Standard / approval | IEC 60332-3-24 Cat. C
Standard / approval | IEC 60754-2 & IEC 61034-2
Standard / approval | ITU-T G.652.D / ISO/IEC 11801
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX HITRONIC FIRE 12E9/125 OS2 FE180/E90 IEC 60331-25 DIN 4102-12 LSZH [year] [meter mark]
Supply | Delivery form: Fumigated export wooden drums or shrink-wrapped coils
Supply | Standard drum lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP