## Request a quote
Request a quotation for GZTACSR
Application engineer · overhead conductors & grid power
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/gztacsr-gap-type-super-thermal-resistant-overhead-conductor/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
GZTACSR Gap-Type Super-Thermal-Resistant Aluminum Alloy Overhead – Dimensions, stranding, breaking load & weights (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/gztacsr-gap-type-super-thermal-resistant-overhead-conductor/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 62420 /IEC 62004. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Nominal area | Stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Rated tensile kN ≈ | Min. sheave R mm | Series
| GZTACSR 50 mm² | 50 mm² | 7/3.00 mm | 9 | 138 | 14.5 | 180 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 95 mm² | 95 mm² | 19/2.52 mm | 12.6 | 262 | 28.2 | 252 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 120 mm² | 120 mm² | 19/2.85 mm | 14.3 | 334 | 36.4 | 286 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 150 mm² | 150 mm² | 26/2.70 + 7/2.10 | 17.1 | 546 | 53.8 | 342 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 185 mm² | 185 mm² | 26/3.00 + 7/2.33 | 19 | 674 | 65.2 | 380 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 240 mm² | 240 mm² | 26/3.44 + 7/2.68 | 21.8 | 885 | 84.5 | 436 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 300 mm² | 300 mm² | 26/3.86 + 7/3.00 | 24.5 | 1110 | 104.2 | 490 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 400 mm² | 400 mm² | 54/3.08 + 7/3.08 | 27.7 | 1432 | 126 | 554 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 500 mm² | 500 mm² | 54/3.44 + 7/3.44 | 31 | 1790 | 156.5 | 620 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
| GZTACSR 630 mm² | 630 mm² | 54/3.86 + 19/2.32 | 34.8 | 2245 | 194 | 696 | GZTACSR Standard Transmission & Distribution Schedule (−40…+210 °C)
Custom kcmil/code-word sizes, grease-filled corrosion protection and non-specular surface finishes available per IEC 62420 /IEC 62004.

## DC resistance & continuous curr
GZTACSR Gap-Type Super-Thermal-Resistant Aluminum Alloy Overhead – DC resistance & continuous current ratings (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/gztacsr-gap-type-super-thermal-resistant-overhead-conductor/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 62420 /IEC 62004. Values for your order are confirmed in the quotation.
Nominal area | Max. DC R₂₀ Ω/km | Continuous current A ≈ | Operating temp.
50 mm² | 0.578 | 210 | −40…+210 °C
95 mm² | 0.304 | 320 | −40…+210 °C
150 mm² | 0.192 | 435 | −40…+210 °C
240 mm² | 0.119 | 590 | −40…+210 °C
400 mm² | 0.072 | 820 | −40…+210 °C
630 mm² | 0.046 | 1080 | −40…+210 °C
Ampacity calculated per IEEE 738 (0.6 m/s wind, 40 °C ambient, 0.5 solar absorptivity / emissivity).

## Technical data
GZTACSR Gap-Type Super-Thermal-Resistant Aluminum Alloy Overhead – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/gztacsr-gap-type-super-thermal-resistant-overhead-conductor/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 62420 /IEC 62004. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | Up to 500 kV AC (Per IEC 62420 /IEC 62004)
Key data | Operating temp. | −40…+210 °C (Continuous thermal rating (IEC 62420))
Key data | Min. bend radius | 20 × OD (Installed / fixed routing)
Key data | Conductor | Extra-high-stren (High-tensile galvanized steel core)
Key data | Outer layer | Trapezoidal (Super-thermal-resistant)
Key data | Standard | IEC 62420 (IEC 62420 /IEC 62004)
Electrical | Rated voltage / duty | Up to 500 kV AC (IEC 62420 /IEC 62004)
Electrical | Conductor construction | Extra-high-strength galvanized steel core & gap — High-tensile galvanized steel core inside a heat-resistant grease-filled annular gap
Electrical | Primary insulation / dielectric | Trapezoidal inner & round outer ZTAL layers — Super-thermal-resistant zirconium-aluminum alloy (ZTAL) layers (+210 °C continuous)
Thermal | Continuous operating temperature | −40…+210 °C per IEC 62420 /IEC 62004
Thermal | Short-circuit / peak thermal limit | +160 °C to +250 °C (5 s adiabatic limit depending on dielectric class)
Thermal | Minimum installation temperature | −5 °C (thermoplastic) / −25 °C (cross-linked or elastomer) / −40 °C (metallic)
Mechanical | Outer protection / covering | Trapezoidal inner & round outer ZTAL layers — Super-thermal-resistant zirconium-aluminum alloy (ZTAL) layers (+210 °C continuous)
Mechanical | Minimum bending radius | 20 × OD (installed / static routing)
Mechanical | Layer count & geometry | 2 concentric/structural layers verified by cross-section inspection
Resistance | Environmental & chemical durability | Engineered for industrial service in accordance with IEC 62420 /IEC 62004
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing product standard | IEC 62420 /IEC 62004
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | GZTACSR
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 7614.10

## Construction
GZTACSR Gap-Type Super-Thermal-Resistant Aluminum Alloy Overhead – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/gztacsr-gap-type-super-thermal-resistant-overhead-conductor/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 62420 /IEC 62004. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Extra-high-strength galvanized steel core & gap | High-tensile galvanized steel core inside a heat-resistant grease-filled annular gap | IEC 62420 /IEC 62004
2 | Trapezoidal inner & round outer ZTAL layers | Super-thermal-resistant zirconium-aluminum alloy (ZTAL) layers (+210 °C continuous) | IEC 62420 /IEC 62004
| GZTACSR — Standard Execution | Built to IEC 62420 /IEC 62004 with extra-high-strength galvanized steel core & gap and trapezoidal inner &
| GZTACSR — Custom Cross-Sections | Full range of metric mm² and AWG/kcmil conductor sizes per IEC 62420 /IEC 62004
| GZTACSR — Export Drum Supply | Supplied with EN 10204 3.1 routine dielectric & conductor resistance test certificate

## Quality and supply
GZTACSR Gap-Type Super-Thermal-Resistant Aluminum Alloy Overhead – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/gztacsr-gap-type-super-thermal-resistant-overhead-conductor/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 62420 /IEC 62004. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (IEC 62420 /IEC 62004) — DC resistance at 20 °C and geometry within IEC 62420 /IEC 62004 class limits | Every manufactured drum / spool
Routine test | Routine dielectric / spark / structural integrity test (IEC 62420 /IEC 62004) — Zero breakdown or structural defect over full production length | Every manufactured drum / spool
Type test | Thermal aging, mechanical & material qualification (IEC 62420 /IEC 62004) — Full compliance with IEC 62420 /IEC 62004 across −40…+210 °C | Type qualification & periodic sample audit
Standard / approval | IEC 62420 Compliant
Standard / approval | EN 10204 3.1 Routine Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX GZTACSR <size> IEC 62420 Up to 500 kV AC CE
Supply | Delivery form: Non-returnable fumigated wooden drums or precision DIN spools
Supply | Standard lengths: 500 m · 1000 m · 2000 m drums (custom cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom production)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP