## Request a quote
Request a quotation for Galvanically Isolated Signal Cable
Application engineer · instrumentation & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/galvanicable-galvanically-isolated-industrial-signal-transmission-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
Galvanically Isolated Industrial Signal Transmission Cable – Dimensions & galvanic isolation ratings (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/galvanicable-galvanically-isolated-industrial-signal-transmission-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 61010-1 / IEC 60664-1 / EN 50288-7. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Pairs & isolation rating | Outer Ø ≈ mm | Weight ≈ kg/km | AC Isolation kV rms | Screen-Screen C pF/m | Series
| Galvanically Isolated Signal Cable 1P×0.50-10KV | 1 Pair × 0.50 mm² · 10 kV AC Twinax | 9.8 | 118 | 10 | 16 | Galvanically Isolated Twinax & Multipair Signal Cables
| Galvanically Isolated Signal Cable 2P×0.50-10KV | 2 Pairs × 0.50 mm² · 10 kV AC | 12.6 | 185 | 10 | 22 | Galvanically Isolated Twinax & Multipair Signal Cables
| Galvanically Isolated Signal Cable 4P×0.50-10KV | 4 Pairs × 0.50 mm² · 10 kV AC | 15.2 | 270 | 10 | 28 | Galvanically Isolated Twinax & Multipair Signal Cables
| Galvanically Isolated Signal Cable 1P×0.75-15KV | 1 Pair × 0.75 mm² · 15 kV AC / 25 kV DC | 12.4 | 172 | 15 | 14 | Galvanically Isolated Twinax & Multipair Signal Cables
Every drum is 100 % routine tested for partial discharge (< 5 pC per IEC 60270) across the galvanic barrier wall.

## Technical data
Galvanically Isolated Industrial Signal Transmission Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/galvanicable-galvanically-isolated-industrial-signal-transmission-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 61010-1 / IEC 60664-1 / EN 50288-7. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Galvanic test | 10 to 15 kV AC (25 kV DC barrier withstand)
Key data | Coupling cap. | ≤ 18 pF/m (Core-to-outer-screen C)
Key data | Impedance | 100 / 120 Ω (Balanced differential pair)
Key data | CMRR @ 1 MHz | ≥ 110 dB (High dV/dt IGBT noise immunity)
Key data | Dual shields | Isolated inner/o (3.0 kV inter-screen barrier)
Key data | Temperature | -40 to +105 °C (XLPE/FEP core · LSZH/PUR jacket)
Electrical | Galvanic isolation withstand | 10 kV AC rms (Standard) · 15 kV AC rms / 25 kV DC (HV Series)
Electrical | Partial discharge extinction | ≥ 6.0 kV rms (< 5 pC partial discharge)
Electrical | Mutual / barrier capacitance | ≤ 38 pF/m (pair) · ≤ 18 pF/m (inner-to-outer screen)
Electrical | Differential impedance | 100 ± 5 Ω or 120 ± 6 Ω (RS-485 / CAN / LVDS compatible)
Thermal | Operating temperature | -40 °C to +105 °C (fixed) · -20 °C to +80 °C (flexing)
Thermal | Short-circuit core rating | +250 °C (FEP / XLPE core)
Thermal | Thermal stability | Zero dielectric shrinkage under impulse heating
Mechanical | Min. bend radius (fixed) | 8 × OD
Mechanical | Min. bend radius (installation) | 12 × OD
Mechanical | Crush & abrasion resistance | ≥ 1,500 N/100 mm crush resistance
Resistance | dV/dt transient immunity | Withstands > 50 kV/µs SiC/IGBT common-mode edges
Resistance | Flame & halogen-free | IEC 60332-1-2, IEC 60332-3-24, IEC 60754-1/2
Resistance | Oil & chemical resistance | EN 60811-404 mineral oil & transformer fluid resistant
Standards | Insulation coordination | IEC 60664-1 & IEC 61010-1 Reinforced Insulation
Standards | Instrumentation construction | EN 50288-7 & IEC 60270 (PD tested)
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Sheath colour | Black with Orange HV-isolation longitudinal stripe
Identification | Customs tariff (HS) | 8544.4993
Identification | Routine test certificate | Includes 100 % AC hi-pot and < 5 pC partial discharge log

## Construction
Galvanically Isolated Industrial Signal Transmission Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/galvanicable-galvanically-isolated-industrial-signal-transmission-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 61010-1 / IEC 60664-1 / EN 50288-7. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Precision-balanced tinned/silver copper pairs | Stranded tinned or silver-plated OFHC copper conductors (0.25, 0.50, 0.75 mm² / 24–18 AWG) twisted with tight lay symmetry
2 | Low-permittivity FEP / cellular XLPE dielectric | Gas-injected cellular XLPE or fluoropolymer FEP primary insulation (εr ≤ 1.65) | Lowers mutual capacitance to ≤ 38 pF/m
| Galvanically Isolated Signal Cable-10KV (1P / 2P × 0.50 mm²) | 10 kV AC rms galvanically isolated twinax/multipair signal cable with dual isolated screens
| Galvanically Isolated Signal Cable-15KV-HV (1P × 0.75 mm²) | 15 kV AC rms / 30 kV impulse galvanically isolated diagnostic cable for MV drives & substations

## Quality and supply
Galvanically Isolated Industrial Signal Transmission Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/galvanicable-galvanically-isolated-industrial-signal-transmission-cable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 61010-1 / IEC 60664-1 / EN 50288-7. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % 10 kV / 15 kV AC barrier hi-pot & IEC 60270 partial discharge test — Zero breakdown for 5 min and PD < 5 pC at 6.0 kV rms | Every manufactured drum length
Type test | 1.2/50 µs lightning/switching impulse withstand test — Withstands 25–30 kV peak impulse between inner and outer screens | Type qualification
Type test | Common-mode rejection & transfer impedance sweep — CMRR ≥ 110 dB @ 1 MHz and ZT ≤ 15 mΩ/m | Type qualification
Standard / approval | IEC 60664-1 & IEC 61010-1
Standard / approval | IEC 60270 Partial Discharge
Standard / approval | EN 50288-7 & RoHS 2
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX Galvanically Isolated Signal Cable 10kV/15kV ISOLATED SIGNAL IEC 60664-1
Supply | Delivery form: Fumigated wooden drums, steel reels or precision spools
Supply | Standard lengths: 500 m · 1000 m (or custom cut/spooled lengths)
Supply | MOQ: 100 m (standard) · 500 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP