## Request a quote
Request a quotation for H05BB-F
Application engineer · harmonised rubber cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h05bb-f-flexible-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H05BB-F Flexible Rubber Cable – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bb-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| H05BB-F 2×0.75 | 2×0.75 | 18 | 5.7 | 6.2 | 14 | 50 | 25 | Harmonised H05BB-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.2)
| H05BB-F 3G0.75 | 3G0.75 | 18 | 6.2 | 6.7 | 22 | 62 | 27 | Harmonised H05BB-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.2)
| H05BB-F 4G0.75 | 4G0.75 | 18 | 6.7 | 7.3 | 29 | 75 | 29 | Harmonised H05BB-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.2)
| H05BB-F 5G0.75 | 5G0.75 | 18 | 7.5 | 8.1 | 36 | 91 | 32 | Harmonised H05BB-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.2)
| H05BB-F 2×1.0 | 2×1.0 | 17 | 6.1 | 6.6 | 19 | 59 | 26 | Harmonised H05BB-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.2)
| H05BB-F 3G1.0 | 3G1.0 | 17 | 6.5 | 7.1 | 29 | 73 | 28 | Harmonised H05BB-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.2)
| H05BB-F 4G1.0 | 4G1.0 | 17 | 7.2 | 7.8 | 38 | 90 | 31 | Harmonised H05BB-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.2)
| H05BB-F 5G1.0 | 5G1.0 | 17 | 7.9 | 8.6 | 48 | 109 | 34 | Harmonised H05BB-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.2)
| 05BB-F 3G1.5 | 3G1.5 | 16 | 8.2 | 8.9 | 43 | 114 | 36 | Extended 05BB-F sizes (1.5–2.5 mm²)
| 05BB-F 4G1.5 | 4G1.5 | 16 | 9.1 | 9.9 | 58 | 142 | 40 | Extended 05BB-F sizes (1.5–2.5 mm²)
| 05BB-F 5G1.5 | 5G1.5 | 16 | 10 | 10.9 | 72 | 174 | 44 | Extended 05BB-F sizes (1.5–2.5 mm²)
| 05BB-F 3G2.5 | 3G2.5 | 14 | 9.8 | 10.6 | 72 | 166 | 42 | Extended 05BB-F sizes (1.5–2.5 mm²)
Dimensions and weights are typical values per EN 50525-2-21 (HD 22.12). Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
H05BB-F Flexible Rubber Cable – Electrical & current ratings (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bb-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
0.75 | 18 | 26 | 12 | 10
1 | 17 | 19.5 | 15 | 13
1.5 | 16 | 13.3 | 23 | 18
2.5 | 14 | 7.98 | 30 | 25
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
H05BB-F Flexible Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bb-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (U0/U · 2.0 kV AC test voltage)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −40…+90 °C (Flexing (−50…+90 °C fixed))
Key data | Bending radius | 4–6 × OD (4 × OD fixed · 6 × OD flexing)
Key data | Compounds | EI6 / EM6 (All-EPR core & sheath (halogen-free))
Key data | Size range | 0.75–2.5 mm² (2 to 5 cores · Class 5 Cu)
Electrical | Rated voltage U0/U | 300/500 V AC
Electrical | Max. operating voltage | 330/550 V AC
Electrical | AC test voltage | 2000 V AC (50 Hz, 15 min)
Electrical | Conductor stranding | IEC 60228 Class 5 fine-stranded bare copper
Electrical | Current rating basis | DIN VDE 0298-4 (+90 °C conductor rating)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −40 °C to +90 °C
Thermal | Temperature, fixed | −50 °C to +90 °C
Mechanical | Min. bending radius, fixed | 4 × overall diameter (OD ≤ 12 mm: 3 × OD)
Mechanical | Min. bending radius, moving | 6 × overall diameter (free movement)
Mechanical | Max. tensile load | 15 N/mm² dynamic (50 N/mm² static)
Mechanical | Sub-zero flexibility | EI6/EM6 EPR remains supple at −40 °C without cracking
Resistance | Ozone, UV & weather | EN 60811-403 ozone-immune EPR outer sheath
Resistance | Halogen-free | IEC 60754-1 halogen-free EI6/EM6 EPR elastomer system
Resistance | Oil contact note | EM6 EPR sheath is for oil-free zones (use H05BN4-F or H05BQ-F for oil)
Resistance | Water & moisture | Resistant to condensation, frost, snow and damp outdoor air
Standards | Construction standard | EN 50525-2-21 (HD 22.12 S2 / DIN VDE 0285-525-2-21)
Standards | Compound standards | EN 50363-1 Type EI6 & EN 50363-2-1 Type EM6
Standards | Selection & installation | EN 50565-1 & EN 50565-2
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black
Identification | Core identification | HD 308 S2 colour code (2 to 5 cores)
Identification | Sheath marking | TEBAOFLEX H05BB-F <HAR> [Size] 300/500V EN 50525-2-21 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
H05BB-F Flexible Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bb-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Fine-stranded bare copper wire (IEC 60228 Class 5) | EN 60228 Class 5
2 | Cold/heat EPR insulation | Cross-linked ethylene-propylene elastomer compound Type EI6 (−40 to +90 °C) | EN 50363-1 EI6
3 | EPR elastomer outer sheath | Cross-linked ethylene-propylene rubber compound Type EM6, black
| H05BB-F (0.75–1.0 mm²) | Harmonised EN 50525-2-21 Table B.2 sizes with EI6/EM6 EPR compounds
| 05BB-F (1.5–2.5 mm²) | Extended 300/500 V sizes for cold-climate and +90 °C appliance connections

## Quality and supply
H05BB-F Flexible Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bb-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — EN 50525-2-21 (HD 22.12) | Type approval
Standard / approval | EN 50525-2-21 (HD 22.12)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H05BB-F 300/500 V [Size] EN 50525-2-21 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request