## Request a quote
Request a quotation for H05BQ-F
Application engineer · PUR & elastomer cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h05bq-f-pur-sheathed-flexible-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H05BQ-F PUR Sheathed Flexible Cable – Dimensions & weights (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| H05BQ-F 2×0.75 | 2×0.75 | 18 | 5.5 | 6 | 14 | 48 | 24 | Harmonised H05BQ-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.4)
| H05BQ-F 3G0.75 | 3G0.75 | 18 | 6 | 6.5 | 22 | 59 | 26 | Harmonised H05BQ-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.4)
| H05BQ-F 4G0.75 | 4G0.75 | 18 | 6.5 | 7.1 | 29 | 72 | 28 | Harmonised H05BQ-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.4)
| H05BQ-F 5G0.75 | 5G0.75 | 18 | 7.3 | 7.9 | 36 | 88 | 32 | Harmonised H05BQ-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.4)
| 05BQ-F 7G0.75 | 7G0.75 | 18 | 8.6 | 9.4 | 50 | 125 | 38 | Multicore 05BQ-F control configurations (7-core)
| H05BQ-F 2×1.0 | 2×1.0 | 17 | 5.9 | 6.4 | 19 | 57 | 26 | Harmonised H05BQ-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.4)
| H05BQ-F 3G1.0 | 3G1.0 | 17 | 6.3 | 6.9 | 29 | 71 | 28 | Harmonised H05BQ-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.4)
| H05BQ-F 4G1.0 | 4G1.0 | 17 | 7 | 7.6 | 38 | 88 | 30 | Harmonised H05BQ-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.4)
| H05BQ-F 5G1.0 | 5G1.0 | 17 | 7.7 | 8.4 | 48 | 106 | 34 | Harmonised H05BQ-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.4)
| 05BQ-F 7G1.0 | 7G1.0 | 17 | 9.2 | 10 | 67 | 152 | 40 | Multicore 05BQ-F control configurations (7-core)
Dimensions and weights are typical values per EN 50525-2-21 (HD 22.10). Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
H05BQ-F PUR Sheathed Flexible Cable – Electrical & current ratings (2)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
0.75 | 18 | 26 | 12 | 10
1 | 17 | 19.5 | 15 | 13
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
H05BQ-F PUR Sheathed Flexible Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (U0/U · 2.0 kV AC test voltage)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −40…+80 °C (Flexing (−50…+90 °C fixed))
Key data | Bending radius | 4–5 × OD (4 × OD fixed · 5 × OD flexing)
Key data | Compounds | EI7 / TMPU (90 °C EPR core · PUR sheath)
Key data | Size range | 0.75–1.0 mm² (2 to 7 cores · Class 5 Cu)
Electrical | Rated voltage U0/U | 300/500 V AC
Electrical | Max. operating voltage | 330/550 V AC
Electrical | AC test voltage | 2000 V AC (50 Hz, 15 min)
Electrical | Conductor stranding | IEC 60228 Class 5 fine-stranded bare copper
Electrical | Current rating basis | DIN VDE 0298-4 (+90 °C EPR conductor rating)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −40 °C to +80 °C
Thermal | Temperature, fixed | −50 °C to +90 °C
Mechanical | Min. bending radius, fixed | 4 × overall diameter
Mechanical | Min. bending radius, moving | 5 × overall diameter (free flexing)
Mechanical | Max. tensile load | 15 N/mm² dynamic (50 N/mm² static)
Mechanical | Abrasion & notch resistance | High tear, cut and abrasion resistance (TMPU per EN 50363-10-2)
Resistance | Oil & coolant resistance | EN 60811-404 mineral oils, greases and cutting emulsions
Resistance | Halogen-free | IEC 60754-1 / EN 60754-1 halogen-free compounds
Resistance | Weather, UV & microbes | Resistant to UV sunlight, ozone, hydrolysis and microbes
Resistance | Water exposure | AD6/AD7 splashing and temporary water immersion
Standards | Construction standard | EN 50525-2-21 (HD 22.10 S2 / DIN VDE 0285-525-2-21)
Standards | Compound standards | EN 50363-1 (EI7 EPR) & EN 50363-10-2 (TMPU PUR)
Standards | Application guide | EN 50565-1 / DIN VDE 0298-300
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Orange (RAL 2003), yellow or black
Identification | Core identification | HD 308 S2 colour code (≤ 5 cores); black numbered (≥ 6 cores)
Identification | Sheath marking | TEBAOFLEX H05BQ-F <HAR> [Size] 300/500V EN 50525-2-21 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
H05BQ-F PUR Sheathed Flexible Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Fine-stranded bare copper wire (IEC 60228 Class 5) | EN 60228 Class 5
2 | Heat-resistant EPR insulation | Cross-linked ethylene-propylene elastomer compound Type EI7 (+90 °C) | EN 50363-1 EI7
3 | Polyurethane outer sheath | Thermoplastic polyurethane elastomer Type TMPU (formerly 11YM1), orange (RAL 2003) or black
| H05BQ-F Orange (RAL 2003) | High-visibility orange TMPU sheath for construction sites and workshop safety
| H05BQ-F Black / Yellow | Optional black or yellow TMPU outer jacket for OEM machinery and stage/industrial leads

## Quality and supply
H05BQ-F PUR Sheathed Flexible Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — EN 50525-2-21 (HD 22.10) | Type approval
Standard / approval | EN 50525-2-21 (HD 22.10)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H05BQ-F 300/500 V [Size] EN 50525-2-21 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request