## Request a quote
Request a quotation for H05RN-F
Application engineer · harmonised rubber cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h05rn-f-flexible-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H05RN-F Flexible Rubber Cable – Dimensions & weights (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05rn-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / IEC 60245-4. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| H05RN-F 2×0.75 | 2×0.75 | 18 | 5.7 | 6.2 | 14 | 52 | 25 | Harmonised H05RN-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.1)
| H05RN-F 3G0.75 | 3G0.75 | 18 | 6.2 | 6.7 | 22 | 64 | 27 | Harmonised H05RN-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.1)
| H05RN-F 4G0.75 | 4G0.75 | 18 | 6.7 | 7.3 | 29 | 78 | 29 | Harmonised H05RN-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.1)
| H05RN-F 2×1.0 | 2×1.0 | 17 | 6.1 | 6.6 | 19 | 61 | 26 | Harmonised H05RN-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.1)
| H05RN-F 3G1.0 | 3G1.0 | 17 | 6.5 | 7.1 | 29 | 76 | 28 | Harmonised H05RN-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.1)
| H05RN-F 4G1.0 | 4G1.0 | 17 | 7.2 | 7.8 | 38 | 94 | 31 | Harmonised H05RN-F sizes (0.75–1.0 mm² per EN 50525-2-21 Table B.1)
| 05RN-F 2×1.5 | 2×1.5 | 16 | 7.5 | 8.2 | 29 | 95 | 33 | Extended 05RN-F industrial sizes (1.5–2.5 mm²)
| 05RN-F 3G1.5 | 3G1.5 | 16 | 8.2 | 8.9 | 43 | 118 | 36 | Extended 05RN-F industrial sizes (1.5–2.5 mm²)
| 05RN-F 4G1.5 | 4G1.5 | 16 | 9.1 | 9.9 | 58 | 148 | 40 | Extended 05RN-F industrial sizes (1.5–2.5 mm²)
| 05RN-F 5G1.5 | 5G1.5 | 16 | 10 | 10.9 | 72 | 182 | 44 | Extended 05RN-F industrial sizes (1.5–2.5 mm²)
| 05RN-F 3G2.5 | 3G2.5 | 14 | 9.8 | 10.6 | 72 | 172 | 42 | Extended 05RN-F industrial sizes (1.5–2.5 mm²)
| 05RN-F 4G2.5 | 4G2.5 | 14 | 10.7 | 11.6 | 96 | 212 | 46 | Extended 05RN-F industrial sizes (1.5–2.5 mm²)
Dimensions and weights are typical values per EN 50525-2-21 / IEC 60245-4. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
H05RN-F Flexible Rubber Cable – Electrical & current ratings (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05rn-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / IEC 60245-4. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
0.75 | 18 | 26 | 12 | 10
1 | 17 | 19.5 | 15 | 13
1.5 | 16 | 13.3 | 23 | 18
2.5 | 14 | 7.98 | 30 | 25
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
H05RN-F Flexible Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05rn-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / IEC 60245-4. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (U0/U · 2.0 kV AC test voltage)
Key data | Conductor temp. | +60 °C max. (+200 °C short-circuit (5 s))
Key data | Ambient temp. | −25…+60 °C (Flexing (−30…+60 °C fixed))
Key data | Bending radius | 4–6 × OD (4 × OD fixed · 6 × OD flexing)
Key data | Compounds | EI4 / EM2 (EPR core · PCP rubber sheath)
Key data | Size range | 0.75–2.5 mm² (2 to 5 cores · Class 5 Cu)
Electrical | Rated voltage U0/U | 300/500 V AC
Electrical | Max. operating voltage | 330/550 V AC
Electrical | AC test voltage | 2000 V AC (50 Hz, 15 min)
Electrical | Conductor class | IEC 60228 / EN 60228 Class 5 flexible copper
Electrical | Current rating basis | DIN VDE 0298-4 / EN 50565-1 (30 °C ambient)
Thermal | Max. conductor temperature | +60 °C continuous operation
Thermal | Short-circuit temperature | +200 °C max. (up to 5 s)
Thermal | Temperature, flexing | −25 °C to +60 °C
Thermal | Temperature, fixed | −30 °C to +60 °C
Mechanical | Min. bending radius, fixed | 4 × overall diameter (OD ≤ 12 mm: 3 × OD)
Mechanical | Min. bending radius, moving | 6 × overall diameter (free flexing)
Mechanical | Max. tensile load | 15 N/mm² dynamic (50 N/mm² static)
Mechanical | Mechanical duty class | Light mechanical stress (EN 50565-2)
Resistance | Oil resistance | EN 60811-404 (EM2 polychloroprene sheath)
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2 single vertical flame
Resistance | UV, weather & ozone | EN 60811-403 ozone-resistant outdoor sheath
Resistance | Water exposure | Damp, wet & outdoor splashing (AD4/AD5)
Standards | Construction standard | EN 50525-2-21 (HD 22.4 S4 / DIN VDE 0285-525-2-21)
Standards | International equivalent | IEC 60245-4 (60245 IEC 57)
Standards | Application guide | EN 50565-1 & EN 50565-2
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black
Identification | Core identification | HD 308 S2 colour code (G = with GN/YE, X = without)
Identification | Sheath marking | TEBAOFLEX H05RN-F <HAR> [Size] 300/500V EN 50525-2-21 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
H05RN-F Flexible Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05rn-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / IEC 60245-4. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Fine-stranded bare copper wire (IEC 60228 Class 5) | EN 60228 Class 5
2 | Elastomeric core insulation | Cross-linked ethylene-propylene rubber compound Type EI4 | EN 50363-1 EI4 (+60 °C)
3 | Outer rubber sheath | Cross-linked polychloroprene (PCP) synthetic elastomer Type EM2, black | EN 50363-2-1 EM2 · oil & weather resistant
| H05RN-F -J (G) | 3 to 5 cores including green-yellow protective earth conductor (HD 308 S2)
| H05RN-F -O (X) | 2-core twin assembly without green-yellow protective conductor (blue, brown)

## Quality and supply
H05RN-F Flexible Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h05rn-f-flexible-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 / IEC 60245-4. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — EN 50525-2-21 / IEC 60245-4 | Type approval
Standard / approval | EN 50525-2-21 / IEC 60245-4
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H05RN-F 300/500 V [Size] EN 50525-2-21 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request