## Request a quote
Request a quotation for H05SS-F & H05SST-F (SiHF)
Application engineer · High-temperature multicore cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/silicone-rubber-multicore-high-temperature-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
Silicone Rubber Multicore High-Temperature Cable (H05SS-F / H05SST-F) – Dimensions, weights & DC resistance (17)
TEBAOFLEX ¦ https://tebaoflex.com/cables/silicone-rubber-multicore-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-83 (H05SS-F & H05SST-F). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Type · Configuration | Cores × CSA mm² | Core wall mm | Sheath mm | Nominal OD mm | Cu mass kg/km | Total mass kg/km | Max. DC res. (20 °C) Ω/km | Series
| H05SS-F · 2×0.75 mm² | 2×0.75 | 0.6 | 0.8 | 6.4 | 14.4 | 54 | 26 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 3G0.75 mm² | 3G0.75 | 0.6 | 0.8 | 6.8 | 21.6 | 66 | 26 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 3G1.0 mm² | 3G1.0 | 0.6 | 0.9 | 7.4 | 28.8 | 79 | 19.5 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 3G1.5 mm² | 3G1.5 | 0.8 | 0.9 | 8.4 | 43.2 | 108 | 13.3 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 4G1.5 mm² | 4G1.5 | 0.8 | 1 | 9.3 | 57.6 | 135 | 13.3 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 5G1.5 mm² | 5G1.5 | 0.8 | 1.1 | 10.3 | 72 | 165 | 13.3 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 7G1.5 mm² | 7G1.5 | 0.8 | 1.1 | 11.2 | 100.8 | 208 | 13.3 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 12G1.5 mm² | 12G1.5 | 0.8 | 1.3 | 14.8 | 172.8 | 345 | 13.3 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 3G2.5 mm² | 3G2.5 | 0.9 | 1.1 | 10.2 | 72 | 162 | 7.98 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 4G2.5 mm² | 4G2.5 | 0.9 | 1.1 | 11.2 | 96 | 202 | 7.98 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 5G2.5 mm² | 5G2.5 | 0.9 | 1.2 | 12.4 | 120 | 248 | 7.98 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 4G4.0 mm² | 4G4.0 | 1 | 1.2 | 13 | 153.6 | 292 | 4.95 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SS-F · 5G6.0 mm² | 5G6.0 | 1 | 1.4 | 16.4 | 288 | 485 | 3.3 | EN 50525-2-83 H05SS-F (SiHF) · 300/500 V · 180 °C · Unbraided Smooth EM9 Silicone Sheath
| H05SST-F · 3G1.5 mm² | 3G1.5 | 0.8 | 0.9 | 9 | 43.2 | 132 | 13.3 | EN 50525-2-83 H05SST-F · 300/500 V · 180 °C · EM9 Silicone Sheath + Protective Outer Braid
| H05SST-F · 4G1.5 mm² | 4G1.5 | 0.8 | 1 | 9.9 | 57.6 | 162 | 13.3 | EN 50525-2-83 H05SST-F · 300/500 V · 180 °C · EM9 Silicone Sheath + Protective Outer Braid
| H05SST-F · 4G2.5 mm² | 4G2.5 | 0.9 | 1.1 | 11.8 | 96 | 238 | 7.98 | EN 50525-2-83 H05SST-F · 300/500 V · 180 °C · EM9 Silicone Sheath + Protective Outer Braid
| H05SST-F · 4G4.0 mm² | 4G4.0 | 1 | 1.2 | 13.7 | 153.6 | 335 | 4.95 | EN 50525-2-83 H05SST-F · 300/500 V · 180 °C · EM9 Silicone Sheath + Protective Outer Braid
'G' denotes constructions including a Green/Yellow protective earth core; '×' denotes constructions without Green/Yellow.

## Technical data
Silicone Rubber Multicore High-Temperature Cable (H05SS-F / H05SST-F) – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/silicone-rubber-multicore-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-83 (H05SS-F & H05SST-F). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Max. operating T | +180 °C (Short-circuit up to +350 °C)
Key data | Rated voltage | 300/500 V (2.0 kV Vac dielectric test)
Key data | Insulation/sheath | EI2 / EM9 SiR (Cross-linked silicone EI2 / EM9)
Key data | Core & CSA range | 2–24C · 0.75–6 (Up to 24 cores (custom to 50 mm²))
Key data | Low-temp limit | −60 °C (Deep-freeze −60 °C flexibility)
Key data | Min. bend radius | 8 × OD / 10 × OD (Fixed 8× · Flexing 10× OD)
Electrical | Rated voltage (U0/U) | U0/U = 300/500 V AC across H05SS-F (unbraided) and H05SST-F (braided)
Electrical | AC test voltage & IR | 2.0 kV Vac AC dielectric test voltage · min. insulation resistance ≥ 200 MΩ·km at 20 °C
Electrical | Conductor stranding & finish | Fine-stranded tinned or bare annealed copper per EN 60228 Class 5
Thermal | Operating & short-circuit temperature | −60 °C to +180 °C continuous conductor temperature (+200 °C short-term peak; +350 °C max 5 s short-circuit)
Thermal | Cryogenic to furnace span | Retains full elastomeric flexibility from −60 °C blast freezers up to +180 °C radiant heat zones
Mechanical | Core, sheath & braid options | EI2 cross-linked silicone cores + EM9 tear-resistant silicone outer sheath (H05SS-F), plus overall treated glass/textile or galvanized steel braid on H05SST-F
Mechanical | Minimum bending radius | 8 × overall diameter (fixed routing) · 10 × overall diameter (free flexing)
Resistance | Flame, smoke & halogen-free | IEC 60332-1-2 flame retardant; halogen-free per IEC 60754-1/2; low smoke density per IEC 61034-2
Resistance | Oils, fats, steam & ozone | Resistant to humid steam, ozone, UV, vegetable/animal fats, alcohols and dilute acids
Standards | Applicable standards | EN 50525-2-83:2011 (DIN VDE 0285-525-2-83 / HD 22.15); EN 60228; HD 308 S2
Standards | Environmental compliance | HAR, CE, RoHS & REACH compliant halogen-free silicone cable
Identification | Core identification | Colour-coded per HD 308 S2 up to 5 cores (with or without G/Y); black cores with white numbers + G/Y from 6 to 24 cores
Identification | Standard outer sheath colours | Reddish-Brown ( oxide red, standard), Black or White

## Construction
Silicone Rubber Multicore High-Temperature Cable (H05SS-F / H05SST-F) – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/silicone-rubber-multicore-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-83 (H05SS-F & H05SST-F). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 tinned/bare copper conductors | Fine-stranded annealed tinned or bare copper per EN 60228 Class 5 (0.75 to 6.0 mm², 2 to 24 cores) | EN 60228
2 | EI2 cross-linked silicone core insulation | Halogen-free vulcanized silicone elastomer compound EI2 per EN 50363-1, colour-coded to HD 308 S2 or black numbered + G/Y | EN 50363-1 / HD 308 S2
3 | EM9 cross-linked silicone outer sheath | Extruded tear- and heat-resistant cross-linked silicone elastomer compound EM9 per EN 50363-2-1 (reddish-brown, black or white) | EN 50363-2-1
4 | Protective outer braid (H05SST-F) | Closely woven treated glass/textile braid or galvanized steel wire braid over the EM9 sheath (applied on H05SST-F; omitted on H05SS-F) | EN 50525-2-83
| H05SS-F (SiHF) · Unbraided Smooth Silicone Sheath | 300/500 V · −60 °C to +180 °C · EI2 silicone cores + smooth EM9 silicone outer sheath for IP68 gland sealing
| H05SST-F (SiHF-GL-P) · Overall Mechanical Braid | 300/500 V · −60 °C to +180 °C · EI2 silicone cores + EM9 silicone sheath + overall textile/glass or galvanized steel wire braid

## Quality and supply
Silicone Rubber Multicore High-Temperature Cable (H05SS-F / H05SST-F) – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/silicone-rubber-multicore-high-temperature-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-83 (H05SS-F & H05SST-F). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC dielectric & spark test — 2.0 kV Vac dielectric test on completed cable and 100% core spark test per EN 50525-2-83 | Every drum
Routine test | Conductor DC resistance check — Verified at 20 °C per EN 60228 Class 5 limits | Every drum
Sample test | Flame & halogen-free test — IEC 60332-1-2 vertical flame test and IEC 60754-1/2 zero-halogen gas acidity check | Production lot
Sample test | EI2 / EM9 thermal endurance & tear test — 180 °C oven aging, −60 °C cold bend and EM9 sheath tear resistance per EN 50363 | Production lot
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX · <HAR> H05SS-F (or H05SST-F) [Cores×mm²] 300/500V EN 50525-2-83 · 180°C · CE
Supply | Delivery form: Coils, non-returnable wooden drums and custom cut lengths
Supply | Lengths: 100 m coils, 500 m / 1,000 m drums and cut-to-length assemblies
Supply | Certificate: EN 10204 3.1 inspection certificate with every dispatch
Supply | Quote response: Engineering specification and quote within 2 business hours
Supply | MOQ: None
Supply | Lead time: None