## Request a quote
Request a quotation for H07BN4-F
Application engineer · heat-resistant & HOFR rubber cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h07bn4-f-heat-resistant-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H07BN4-F Heat-Resistant Rubber Cable – Dimensions & weights (23)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bn4-f-heat-resistant-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| H07BN4-F 1×16 | 1×16 | 6 | 9.9 | 10.8 | 154 | 235 | 43 | Single-core H07BN4-F power & loadbank leads (16–240 mm²)
| H07BN4-F 1×35 | 1×35 | 2 | 13.2 | 14.3 | 336 | 445 | 57 | Single-core H07BN4-F power & loadbank leads (16–240 mm²)
| H07BN4-F 1×50 | 1×50 | 1 | 15.2 | 16.5 | 480 | 620 | 66 | Single-core H07BN4-F power & loadbank leads (16–240 mm²)
| H07BN4-F 1×70 | 1×70 | 2/0 | 17.1 | 18.6 | 672 | 835 | 74 | Single-core H07BN4-F power & loadbank leads (16–240 mm²)
| H07BN4-F 1×95 | 1×95 | 3/0 | 19.3 | 21 | 912 | 1110 | 84 | Single-core H07BN4-F power & loadbank leads (16–240 mm²)
| H07BN4-F 1×120 | 1×120 | 4/0 | 21.3 | 23.2 | 1152 | 1380 | 93 | Single-core H07BN4-F power & loadbank leads (16–240 mm²)
| H07BN4-F 1×185 | 1×185 | 350 kcmil | 25.8 | 28 | 1776 | 2060 | 112 | Single-core H07BN4-F power & loadbank leads (16–240 mm²)
| H07BN4-F 1×240 | 1×240 | 500 kcmil | 29 | 31.5 | 2304 | 2650 | 126 | Single-core H07BN4-F power & loadbank leads (16–240 mm²)
| H07BN4-F 3G1.5 | 3G1.5 | 16 | 9 | 9.8 | 43 | 135 | 39 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G1.5 | 4G1.5 | 16 | 9.9 | 10.8 | 58 | 168 | 43 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 5G1.5 | 5G1.5 | 16 | 10.9 | 11.9 | 72 | 205 | 48 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 3G2.5 | 3G2.5 | 14 | 10.7 | 11.6 | 72 | 198 | 46 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G2.5 | 4G2.5 | 14 | 11.8 | 12.8 | 96 | 245 | 51 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 5G2.5 | 5G2.5 | 14 | 13.1 | 14.2 | 120 | 305 | 57 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G4 | 4G4 | 12 | 13.6 | 14.8 | 154 | 355 | 59 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 5G4 | 5G4 | 12 | 15.1 | 16.4 | 192 | 438 | 66 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G6 | 4G6 | 10 | 15.5 | 16.8 | 230 | 485 | 67 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 5G6 | 5G6 | 10 | 17.3 | 18.8 | 288 | 598 | 75 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G10 | 4G10 | 8 | 20.1 | 21.8 | 384 | 845 | 87 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G16 | 4G16 | 6 | 23.2 | 25.2 | 614 | 1190 | 101 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G25 | 4G25 | 4 | 28 | 30.4 | 960 | 1760 | 122 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G35 | 4G35 | 2 | 31.5 | 34.2 | 1344 | 2320 | 137 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
| H07BN4-F 4G50 | 4G50 | 1 | 36.4 | 39.6 | 1920 | 3190 | 158 | Multicore H07BN4-F heavy-duty power & control cables (3G1.5–4G50)
Dimensions and weights are typical values per EN 50525-2-21 (HD 22.12). Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
H07BN4-F Heat-Resistant Rubber Cable – Electrical & current ratings (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bn4-f-heat-resistant-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
1.5 | 16 | 13.3 | 23 | 18
2.5 | 14 | 7.98 | 30 | 25
4 | 12 | 4.95 | 41 | 34
6 | 10 | 3.3 | 53 | 44
10 | 8 | 1.91 | 74 | 61
16 | 6 | 1.21 | 99 | 82
25 | 4 | 0.78 | 131 | 108
35 | 2 | 0.554 | 162 | 135
50 | 1 | 0.386 | 202 | 168
70 | 2/0 | 0.272 | 250 | 207
95 | 3/0 | 0.206 | 301 | 250
120 | 4/0 | 0.161 | 352 | 292
185 | 350 kcmil | 0.106 | 461 | 382
240 | 500 kcmil | 0.08 | 540 | 453
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
H07BN4-F Heat-Resistant Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bn4-f-heat-resistant-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (0.6/1 kV fixed protected · 2.5 kV test)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −25…+90 °C (Flexing (−40…+90 °C fixed))
Key data | Bending radius | 4–8 × OD (4–6 × OD fixed · 6–8 × OD flexing)
Key data | Compounds | EI7 / EM7 (90 °C EPR core · 90 °C CSP sheath)
Key data | Size range | 1.5–240 mm² (1 to 5 cores · Class 5 Cu)
Electrical | Rated voltage U0/U | 450/750 V AC (0.6/1 kV fixed protected)
Electrical | Max. operating voltage | 495/825 V AC (up to 1000 V AC protected)
Electrical | AC test voltage | 2500 V AC (50 Hz, 15 min)
Electrical | Conductor stranding | IEC 60228 Class 5 fine-stranded copper
Electrical | Current rating basis | DIN VDE 0298-4 / BS 7671 (+90 °C thermoset rating)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −25 °C to +90 °C
Thermal | Temperature, fixed | −40 °C to +90 °C
Mechanical | Min. bending radius, fixed | 4 × OD (OD ≤ 25 mm) · 6 × OD (OD > 25 mm)
Mechanical | Min. bending radius, moving | 6 × OD (OD ≤ 25 mm) · 8 × OD (OD > 25 mm)
Mechanical | Max. tensile load | 15 N/mm² dynamic (50 N/mm² static)
Mechanical | Mechanical impact class | Heavy mechanical duty (EN 50565-2)
Resistance | Oil & fuel resistance | EN 60811-404 mineral oils, diesel & hydraulic fluids (EM7)
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2 self-extinguishing
Resistance | Heat & ozone endurance | EM7 CSP sheath resists +90 °C thermal ageing & EN 60811-403 ozone
Resistance | Water exposure | AD6/AD7 outdoor rain, washdown and temporary immersion
Standards | Construction standard | EN 50525-2-21 (HD 22.12 S2 / BS 7919 / DIN VDE 0285-525-2-21)
Standards | Compound standards | EN 50363-1 Type EI7 & EN 50363-2-1 Type EM7 (HOFR)
Standards | Selection & installation | EN 50565-1 / BS 7671
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black
Identification | Core identification | HD 308 S2 colour code (up to 5 cores)
Identification | Sheath marking | TEBAOFLEX H07BN4-F <HAR> [Size] 450/750V 90°C EN 50525-2-21 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
H07BN4-F Heat-Resistant Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bn4-f-heat-resistant-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Fine-stranded bare or tinned copper wire (IEC 60228 Class 5) | EN 60228 Class 5
2 | Separator tape | Non-hygroscopic polyester foil separator over conductor on larger cross-sections
3 | Heat-resistant EPR insulation | Cross-linked ethylene-propylene elastomer Type EI7 (+90 °C) | EN 50363-1 EI7
4 | Heavy-duty HOFR outer sheath | Cross-linked chlorosulphonated polyethylene (CSP) / elastomer Type EM7, black
| H07BN4-F Single-Core (1×1.5–1×240) | High-current single-core power tails for generators, loadbanks and busbar links (0.6/1 kV protected)
| H07BN4-F Multicore (2–5C, 1.5–95) | Multi-core heavy-duty trailing and machine feeder cables with HD 308 S2 colour-coded cores

## Quality and supply
H07BN4-F Heat-Resistant Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bn4-f-heat-resistant-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.12). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.5 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — EN 50525-2-21 (HD 22.12) | Type approval
Standard / approval | EN 50525-2-21 (HD 22.12)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H07BN4-F 450/750 V 90°C [Size] EN 50525-2-21 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request