## Request a quote
Request a quotation for H07BQ-F
Application engineer · PUR & elastomer cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h07bq-f-pur-sheathed-flexible-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H07BQ-F PUR Sheathed Flexible Cable – Dimensions & weights (21)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| H07BQ-F 2×1.5 | 2×1.5 | 16 | 7.7 | 8.4 | 29 | 92 | 34 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 3G1.5 | 3G1.5 | 16 | 8.4 | 9.1 | 43 | 115 | 36 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 4G1.5 | 4G1.5 | 16 | 9.2 | 10 | 58 | 144 | 40 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 5G1.5 | 5G1.5 | 16 | 10.1 | 11 | 72 | 178 | 44 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| 07BQ-F 7G1.5 | 7G1.5 | 16 | 12.3 | 13.4 | 101 | 255 | 54 | Extended 07BQ-F multicore & heavy power sizes (7–12 cores & 35–50 mm²)
| 07BQ-F 12G1.5 | 12G1.5 | 16 | 15.5 | 16.8 | 173 | 410 | 67 | Extended 07BQ-F multicore & heavy power sizes (7–12 cores & 35–50 mm²)
| H07BQ-F 3G2.5 | 3G2.5 | 14 | 9.9 | 10.8 | 72 | 172 | 43 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 4G2.5 | 4G2.5 | 14 | 10.9 | 11.9 | 96 | 215 | 48 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 5G2.5 | 5G2.5 | 14 | 12.1 | 13.2 | 120 | 268 | 53 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| 07BQ-F 7G2.5 | 7G2.5 | 14 | 14.5 | 15.8 | 168 | 375 | 63 | Extended 07BQ-F multicore & heavy power sizes (7–12 cores & 35–50 mm²)
| H07BQ-F 4G4 | 4G4 | 12 | 12.9 | 14 | 154 | 320 | 56 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 5G4 | 5G4 | 12 | 14.4 | 15.6 | 192 | 395 | 62 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 4G6 | 4G6 | 10 | 14.6 | 15.9 | 230 | 445 | 64 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 5G6 | 5G6 | 10 | 16.4 | 17.8 | 288 | 555 | 71 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 4G10 | 4G10 | 8 | 19.1 | 20.8 | 384 | 780 | 83 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 5G10 | 5G10 | 8 | 21.1 | 22.9 | 480 | 965 | 92 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 4G16 | 4G16 | 6 | 22.1 | 24 | 614 | 1110 | 96 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 5G16 | 5G16 | 6 | 24.7 | 26.8 | 768 | 1385 | 107 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| H07BQ-F 4G25 | 4G25 | 4 | 26.9 | 29.2 | 960 | 1660 | 117 | Harmonised H07BQ-F power & control sizes (1.5–25 mm² per EN 50525-2-21 Table B.4)
| 07BQ-F 4G35 | 4G35 | 2 | 30.2 | 32.8 | 1344 | 2190 | 131 | Extended 07BQ-F multicore & heavy power sizes (7–12 cores & 35–50 mm²)
| 07BQ-F 4G50 | 4G50 | 1 | 35.1 | 38.2 | 1920 | 3040 | 153 | Extended 07BQ-F multicore & heavy power sizes (7–12 cores & 35–50 mm²)
Dimensions and weights are typical values per EN 50525-2-21 (HD 22.10). Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
H07BQ-F PUR Sheathed Flexible Cable – Electrical & current ratings (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
1.5 | 16 | 13.3 | 23 | 18
2.5 | 14 | 7.98 | 30 | 25
4 | 12 | 4.95 | 41 | 34
6 | 10 | 3.3 | 53 | 44
10 | 8 | 1.91 | 74 | 61
16 | 6 | 1.21 | 99 | 82
25 | 4 | 0.78 | 131 | 108
35 | 2 | 0.554 | 162 | 135
50 | 1 | 0.386 | 202 | 168
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
H07BQ-F PUR Sheathed Flexible Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (0.6/1 kV fixed protected · 2.5 kV test)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −40…+80 °C (Flexing (−50…+90 °C fixed))
Key data | Bending radius | 4–5 × OD (4 × OD fixed · 5 × OD flexing)
Key data | Compounds | EI7 / TMPU (90 °C EPR core · PUR sheath)
Key data | Size range | 1.5–50 mm² (2 to 12 cores · Class 5 Cu)
Electrical | Rated voltage U0/U | 450/750 V AC (0.6/1 kV fixed protected)
Electrical | Max. operating voltage | 495/825 V AC (up to 1000 V protected)
Electrical | AC test voltage | 2500 V AC (50 Hz, 15 min)
Electrical | Conductor stranding | IEC 60228 Class 5 fine-stranded bare copper
Electrical | Current rating basis | DIN VDE 0298-4 (+90 °C EPR conductor rating)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −40 °C to +80 °C
Thermal | Temperature, fixed | −50 °C to +90 °C
Mechanical | Min. bending radius, fixed | 4 × overall diameter
Mechanical | Min. bending radius, moving | 5 × overall diameter (free flexing)
Mechanical | Max. tensile load | 15 N/mm² dynamic (50 N/mm² static)
Mechanical | Abrasion & tear strength | TMPU polyurethane per EN 50363-10-2 (high cut/notch resistance)
Resistance | Oil & chemical resistance | EN 60811-404 mineral oils, hydraulic fluids, coolants & alkalis
Resistance | Halogen-free | IEC 60754-1 / EN 60754-1 halogen-free compounds
Resistance | Weather, UV & microbes | Resistant to UV sunlight, ozone, hydrolysis and microbial attack
Resistance | Water exposure | AD6/AD7 washdown and temporary immersion
Standards | Construction standard | EN 50525-2-21 (HD 22.10 S2 / DIN VDE 0285-525-2-21)
Standards | Compound standards | EN 50363-1 (EI7 EPR) & EN 50363-10-2 (TMPU PUR)
Standards | Application guide | EN 50565-1 / DIN VDE 0298-300
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Orange (RAL 2003), yellow or black
Identification | Core identification | HD 308 S2 colour code (≤ 5 cores); black numbered + GN/YE (≥ 7 cores)
Identification | Sheath marking | TEBAOFLEX H07BQ-F <HAR> [Size] 450/750V EN 50525-2-21 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
H07BQ-F PUR Sheathed Flexible Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Fine-stranded bare copper wire (IEC 60228 Class 5) | EN 60228 Class 5
2 | Heat-resistant EPR insulation | Cross-linked ethylene-propylene elastomer compound Type EI7 (+90 °C) | EN 50363-1 EI7
3 | Inner elastomeric filler | Extruded elastomeric filler / inner bedding on multi-core sizes
4 | Polyurethane outer sheath | Heavy-duty thermoplastic polyurethane elastomer Type TMPU (11YM1), orange (RAL 2003)
| H07BQ-F (2–5 cores, 1.5–25 mm²) | Harmonised EN 50525-2-21 Table B.4 sizes with HD 308 S2 colour-coded EI7 cores
| 07BQ-F (7–12 cores & ≥ 35 mm²) | Extended control and high-power sizes built to EN 50525-2-21 compound specifications

## Quality and supply
H07BQ-F PUR Sheathed Flexible Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07bq-f-pur-sheathed-flexible-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-21 (HD 22.10). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.5 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — EN 50525-2-21 (HD 22.10) | Type approval
Standard / approval | EN 50525-2-21 (HD 22.10)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H07BQ-F 450/750 V [Size] EN 50525-2-21 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request