## Request a quote
Request a quotation for H07G-K
Application engineer · high-temperature, ignition & UHV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h07g-k-flexible-eva-heat-resistant-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H07G-K Flexible EVA Heat-Resistant Wire – Dimensions & weights (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-k-flexible-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section / size | Conductor build | Wall ≈ mm | Outer Ø ≈ mm | Metal kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| H07G-K 1×0.5 | 0.5 | 16×0.25 mm Cl.5 | 0.6 | 2.1 | 4.8 | 8.8 | 8 | Standard H07G-K configurations
| H07G-K 1×0.75 | 0.75 | 16×0.25 mm Cl.5 | 0.6 | 2.4 | 7.2 | 12.2 | 10 | Standard H07G-K configurations
| H07G-K 1×1 | 1 | 20×0.25 mm Cl.5 | 0.6 | 2.5 | 9.6 | 14.7 | 10 | Standard H07G-K configurations
| H07G-K 1×1.5 | 1.5 | 31×0.25 mm Cl.5 | 0.8 | 3.2 | 14.4 | 23 | 13 | Standard H07G-K configurations
| H07G-K 1×2.5 | 2.5 | 51×0.25 mm Cl.5 | 0.9 | 3.9 | 24 | 36.3 | 16 | Standard H07G-K configurations
| H07G-K 1×4 | 4 | 82×0.25 mm Cl.5 | 1 | 4.7 | 38.4 | 55.5 | 19 | Standard H07G-K configurations
| H07G-K 1×6 | 6 | 122×0.25 mm Cl.5 | 1 | 5.3 | 57.6 | 77.5 | 21 | Standard H07G-K configurations
| H07G-K 1×10 | 10 | 141×0.30 mm Cl.5 | 1.2 | 6.6 | 96 | 125.4 | 26 | Standard H07G-K configurations
| H07G-K 1×16 | 16 | 225×0.30 mm Cl.5 | 1.2 | 7.7 | 153.6 | 188.8 | 31 | Standard H07G-K configurations
| H07G-K 1×25 | 25 | 352×0.30 mm Cl.5 | 1.4 | 9.5 | 240 | 292.3 | 48 | Standard H07G-K configurations
| H07G-K 1×35 | 35 | 493×0.30 mm Cl.5 | 1.4 | 10.7 | 336 | 395.7 | 54 | Standard H07G-K configurations
| H07G-K 1×50 | 50 | 704×0.30 mm Cl.5 | 1.6 | 12.6 | 480 | 559.9 | 63 | Standard H07G-K configurations
| H07G-K 1×70 | 70 | 986×0.30 mm Cl.5 | 1.6 | 14.3 | 672 | 763.6 | 72 | Standard H07G-K configurations
| H07G-K 1×95 | 95 | 1338×0.30 mm Cl.5 | 1.8 | 16.6 | 912 | 1034 | 83 | Standard H07G-K configurations
| H07G-K 1×120 | 120 | 1690×0.30 mm Cl.5 | 1.8 | 18.2 | 1152 | 1286.9 | 91 | Standard H07G-K configurations
Outer diameters and weights are nominal engineering values for H07G-K subject to standard manufacturing tolerances per EN 50525-2-42 / DIN VDE 0285-525-2-42.

## Electrical & rating data
H07G-K Flexible EVA Heat-Resistant Wire – Electrical & rating data (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-k-flexible-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Primary rating (A or kV) | Derated / AC rating | Dielectric test V AC rms
1×0.5 mm² | 40.1 | 12 | 9 | 2500
1×0.75 mm² | 26.7 | 16 | 12 | 2500
1×1 mm² | 20 | 20 | 15 | 2500
1×1.5 mm² | 13.7 | 26 | 20 | 2500
1×2.5 mm² | 8.21 | 36 | 28 | 2500
1×4 mm² | 5.09 | 49 | 37 | 2500
1×6 mm² | 3.39 | 63 | 48 | 2500
1×10 mm² | 1.95 | 86 | 66 | 2500
1×16 mm² | 1.24 | 115 | 88 | 2500
1×25 mm² | 0.795 | 149 | 114 | 2500
1×35 mm² | 0.565 | 185 | 142 | 2500
1×50 mm² | 0.393 | 225 | 172 | 2500
1×70 mm² | 0.277 | 289 | 221 | 2500
1×95 mm² | 0.21 | 352 | 269 | 2500
1×120 mm² | 0.164 | 410 | 314 | 2500
Electrical resistance at +20 °C and dielectric withstand voltages verified per EN 50525-2-42 / DIN VDE 0285-525-2-42.

## Technical data
H07G-K Flexible EVA Heat-Resistant Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-k-flexible-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (U0/U · up to 0.6/1 kV protected)
Key data | Max temperature | +110 °C (Continuous · +120 °C short-term)
Key data | Conductor | Sn-Cu Class 5 (Fine-stranded tinned copper)
Key data | Insulation | EVA Type EI3 (Cross-linked halogen-free rubber)
Key data | Min bend radius | 4–6 × OD fixed (4 × OD ≤ 8 mm; 6 × OD > 12 mm)
Key data | Size range | 0.5 to 120 mm² (Control hook-up to power leads)
Electrical | Rated voltage U0/U | 450/750 V AC
Electrical | Protected cabinet voltage | 600/1000 V AC in protected switchgear
Electrical | AC test voltage | 2500 V AC (50 Hz, 5 min)
Electrical | Insulation resistance | ≥ 200 MΩ·km at +20 °C
Electrical | Current rating basis | DIN VDE 0298-4 (+110 °C single-core in air)
Thermal | Continuous conductor temp. | -40 °C to +110 °C
Thermal | Short-term peak temperature | +120 °C (up to 1000 h)
Thermal | Short-circuit temperature | +250 °C (max. 5 s)
Thermal | Min. installation temp. | -25 °C
Mechanical | Conductor stranding | IEC 60228 Class 5 fine-stranded tinned Cu
Mechanical | Min. bending radius (≤ 8 mm OD) | 4 × overall diameter (fixed)
Mechanical | Min. bending radius (> 8 mm OD) | 5 × OD (8–12 mm) · 6 × OD (> 12 mm)
Mechanical | Tensile load limit | 15 N/mm² during installation routing
Resistance | Flame retardance | IEC 60332-1-2 vertical single-wire test
Resistance | Halogen-free verification | IEC 60754-1 & IEC 60754-2
Resistance | Ozone & varnish resistance | EN 60811-403 ozone & impregnating resins
Standards | Construction standard | EN 50525-2-42 / DIN VDE 0285-525-2-42
Standards | Conductor standard | IEC 60228 Class 5 tinned copper
Standards | RoHS & REACH | RoHS 3 & REACH compliant
Identification | Standard colours | Black, blue, brown, red, white, grey, GNYE
Identification | Surface marking | TEBAOFLEX H07G-K <HAR> [mm²] EN 50525-2-42
Identification | Customs tariff (HS) | 8544.49

## Construction
H07G-K Flexible EVA Heat-Resistant Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-k-flexible-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Fine-stranded tinned copper | Electrolytic tinned copper wire, fine-stranded (IEC 60228 Class 5)
2 | Separator tape (≥ 25 mm²) | Thin heat-resistant polyester foil wrap
3 | Cross-linked EVA EI3 dielectric | Ethylene-vinyl acetate elastomer compound Type EI3 (EN 50363-1)
4 | Halogen-free outer skin | Smooth colour-coded EI3 EVA outer surface
| H07G-K (1.5–120 mm²) | Harmonised 450/750 V Class 5 flexible EVA single-core wire per EN 50525-2-42
| 05G-K (0.5–1.0 mm²) | 300/500 V fine-stranded EVA control wire for compact electronic sub-racks and luminaires

## Quality and supply
H07G-K Flexible EVA Heat-Resistant Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-k-flexible-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Dielectric spark / high-voltage withstand test — 100 % in-line spark and AC/DC dielectric withstand per EN 50525-2-42 / DIN VDE 0285-525-2-42 | Every manufactured length
Routine test | Conductor DC resistance & continuity check — Within maximum 20 °C resistance limit specified for H07G-K | Every spool or drum length
Sample test | Thermal ageing & dimensional verification — Wall thickness, concentricity and post-ageing elongation per EN 50525-2-42 / DIN VDE 0285-525-2-42 | Per production batch
Type test | Flame, outgassing or high-temperature endurance — Qualified to EN 50525-2-42 / DIN VDE 0285-525-2-42 thermal and environmental performance criteria | Type qualification
Standard / approval | EN 50525-2-42 / DIN VDE 0285-525-2-42
Standard / approval | CE (2014/35/EU) & RoHS 3 (2015/863/EU) Compliant
Standard / approval | REACH SVHC & Halogen/Asbestos Compliance Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H07G-K 450/750 V 1×4.0 EN 50525-2-42 CE
Supply | Delivery form: Precision spools, coils or export wooden drums
Supply | Standard lengths: 50 m · 100 m · 500 m · 1000 m (or cut harnesses)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP