## Request a quote
Request a quotation for H07G-R
Application engineer · high-temperature, ignition & UHV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h07g-r-stranded-eva-heat-resistant-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H07G-R Stranded EVA Heat-Resistant Wire – Dimensions & weights (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-r-stranded-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section / size | Conductor build | Wall ≈ mm | Outer Ø ≈ mm | Metal kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| H07G-R 1×1.5 | 1.5 | 7×0.52 mm Cl.2 | 0.8 | 3.2 | 14.4 | 23.2 | 13 | Standard H07G-R configurations
| H07G-R 1×2.5 | 2.5 | 7×0.67 mm Cl.2 | 0.9 | 3.8 | 24 | 35.7 | 15 | Standard H07G-R configurations
| H07G-R 1×4 | 4 | 7×0.85 mm Cl.2 | 1 | 4.6 | 38.4 | 55 | 18 | Standard H07G-R configurations
| H07G-R 1×6 | 6 | 7×1.04 mm Cl.2 | 1 | 5.2 | 57.6 | 77.1 | 21 | Standard H07G-R configurations
| H07G-R 1×10 | 10 | 7×1.35 mm Cl.2 | 1.2 | 6.5 | 96 | 125.3 | 26 | Standard H07G-R configurations
| H07G-R 1×16 | 16 | 7×1.71 mm Cl.2 | 1.2 | 7.5 | 153.6 | 187.5 | 30 | Standard H07G-R configurations
| H07G-R 1×25 | 25 | 7×2.13 mm Cl.2 | 1.4 | 9.2 | 240 | 289.3 | 46 | Standard H07G-R configurations
| H07G-R 1×35 | 35 | 7×2.52 mm Cl.2 | 1.4 | 10.4 | 336 | 393.2 | 52 | Standard H07G-R configurations
| H07G-R 1×50 | 50 | 19×1.83 mm Cl.2 | 1.6 | 12.3 | 480 | 558.1 | 62 | Standard H07G-R configurations
| H07G-R 1×70 | 70 | 19×2.17 mm Cl.2 | 1.6 | 14 | 672 | 763.3 | 70 | Standard H07G-R configurations
| H07G-R 1×95 | 95 | 19×2.52 mm Cl.2 | 1.8 | 16.1 | 912 | 1028.2 | 80 | Standard H07G-R configurations
Outer diameters and weights are nominal engineering values for H07G-R subject to standard manufacturing tolerances per EN 50525-2-42 / DIN VDE 0285-525-2-42.

## Electrical & rating data
H07G-R Stranded EVA Heat-Resistant Wire – Electrical & rating data (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-r-stranded-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Primary rating (A or kV) | Derated / AC rating | Dielectric test V AC rms
1×1.5 mm² | 12.2 | 26 | 20 | 2500
1×2.5 mm² | 7.56 | 36 | 28 | 2500
1×4 mm² | 4.7 | 49 | 37 | 2500
1×6 mm² | 3.11 | 63 | 48 | 2500
1×10 mm² | 1.84 | 86 | 66 | 2500
1×16 mm² | 1.16 | 115 | 88 | 2500
1×25 mm² | 0.734 | 149 | 114 | 2500
1×35 mm² | 0.529 | 185 | 142 | 2500
1×50 mm² | 0.391 | 225 | 172 | 2500
1×70 mm² | 0.27 | 289 | 221 | 2500
1×95 mm² | 0.195 | 352 | 269 | 2500
Electrical resistance at +20 °C and dielectric withstand voltages verified per EN 50525-2-42 / DIN VDE 0285-525-2-42.

## Technical data
H07G-R Stranded EVA Heat-Resistant Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-r-stranded-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (U0/U · 2500 V AC test voltage)
Key data | Max temperature | +110 °C (Continuous conductor · +120 °C peak)
Key data | Conductor | Sn-Cu Class 2 (7/19-wire rigid stranded tinned Cu)
Key data | Insulation | EVA Type EI3 (Cross-linked halogen-free EVA)
Key data | Min bend radius | 4–6 × OD fixed (4 × OD ≤ 8 mm; 5–6 × OD larger)
Key data | Size range | 1.5 to 95 mm² (EN 50525-2-42 Class 2 power range)
Electrical | Rated voltage U0/U | 450/750 V AC
Electrical | Protected installation voltage | 600/1000 V AC inside enclosed switchgear
Electrical | AC dielectric test voltage | 2500 V AC for 5 min in water bath
Electrical | Insulation resistance | ≥ 200 MΩ·km at +20 °C
Electrical | Current rating basis | DIN VDE 0298-4 (+110 °C conductor table)
Thermal | Continuous operating temp. | -40 °C to +110 °C at conductor
Thermal | Short-term peak temperature | +120 °C
Thermal | Max. short-circuit temperature | +250 °C (5 s max.)
Thermal | Thermal ageing test | 240 h at +150 °C per EN 60811-401
Mechanical | Conductor class | IEC 60228 Class 2 (7 or 19 wires)
Mechanical | Min. bending radius (≤ 8 mm OD) | 4 × overall diameter (fixed)
Mechanical | Min. bending radius (> 8 mm OD) | 5 × OD (8–12 mm) · 6 × OD (> 12 mm)
Mechanical | Max. tensile pulling load | 50 N/mm² of copper cross-section
Resistance | Flame propagation | Self-extinguishing to IEC 60332-1-2
Resistance | Halogen & acid gas | Halogen-free per IEC 60754-1 & -2
Resistance | Ozone resistance | EN 60811-403 Method A / B compliant
Standards | Product standard | EN 50525-2-42 / DIN VDE 0285-525-2-42
Standards | Conductor standard | IEC 60228 Table 2 Class 2 tinned copper
Standards | RoHS & REACH | RoHS 3 (2015/863/EU) & REACH compliant
Identification | Core colours | Black, blue, brown, red, white, GNYE
Identification | Marking legend | TEBAOFLEX H07G-R <HAR> [mm²] EN 50525-2-42
Identification | Customs tariff (HS) | 8544.49

## Construction
H07G-R Stranded EVA Heat-Resistant Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-r-stranded-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 2 stranded tinned copper | 7-wire or 19-wire concentric stranded tinned copper (IEC 60228 Class 2)
2 | Separator foil (≥ 16 mm²) | Heat-resistant polyester separator tape over conductor
3 | Cross-linked EVA EI3 wall | Ethylene-vinyl acetate thermoset compound Type EI3 (EN 50363-1)
4 | Halogen-free outer finish | Extruded smooth EI3 outer surface in standard VDE colours
| H07G-R 7-wire (1.5–35 mm²) | 7-strand concentric tinned copper conductor with EI3 EVA insulation
| H07G-R 19-wire (50–95 mm²) | 19-strand concentric tinned copper feeder conductor for high-current furnace bus drops

## Quality and supply
H07G-R Stranded EVA Heat-Resistant Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-r-stranded-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Dielectric spark / high-voltage withstand test — 100 % in-line spark and AC/DC dielectric withstand per EN 50525-2-42 / DIN VDE 0285-525-2-42 | Every manufactured length
Routine test | Conductor DC resistance & continuity check — Within maximum 20 °C resistance limit specified for H07G-R | Every spool or drum length
Sample test | Thermal ageing & dimensional verification — Wall thickness, concentricity and post-ageing elongation per EN 50525-2-42 / DIN VDE 0285-525-2-42 | Per production batch
Type test | Flame, outgassing or high-temperature endurance — Qualified to EN 50525-2-42 / DIN VDE 0285-525-2-42 thermal and environmental performance criteria | Type qualification
Standard / approval | EN 50525-2-42 / DIN VDE 0285-525-2-42
Standard / approval | CE (2014/35/EU) & RoHS 3 (2015/863/EU) Compliant
Standard / approval | REACH SVHC & Halogen/Asbestos Compliance Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H07G-R 450/750 V 1×10 EN 50525-2-42 CE
Supply | Delivery form: Precision spools, coils or export wooden drums
Supply | Standard lengths: 50 m · 100 m · 500 m · 1000 m (or cut harnesses)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP