## Request a quote
Request a quotation for H07G-U
Application engineer · high-temperature, ignition & UHV cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h07g-u-solid-conductor-eva-heat-resistant-wire/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H07G-U Solid-Conductor EVA Heat-Resistant Wire – Dimensions & weights (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-u-solid-conductor-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cross-section / size | Conductor build | Wall ≈ mm | Outer Ø ≈ mm | Metal kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| H07G-U 1×0.5 | 0.5 | 1×0.80 mm solid | 0.6 | 2 | 4.8 | 8.6 | 8 | Standard H07G-U configurations
| H07G-U 1×0.75 | 0.75 | 1×0.98 mm solid | 0.6 | 2.2 | 7.2 | 11.6 | 9 | Standard H07G-U configurations
| H07G-U 1×1 | 1 | 1×1.13 mm solid | 0.6 | 2.4 | 9.6 | 14.7 | 10 | Standard H07G-U configurations
| H07G-U 1×1.5 | 1.5 | 1×1.38 mm solid | 0.8 | 3 | 14.4 | 22.4 | 12 | Standard H07G-U configurations
| H07G-U 1×2.5 | 2.5 | 1×1.78 mm solid | 0.9 | 3.6 | 24 | 35 | 14 | Standard H07G-U configurations
| H07G-U 1×4 | 4 | 1×2.26 mm solid | 1 | 4.3 | 38.4 | 53.4 | 17 | Standard H07G-U configurations
| H07G-U 1×6 | 6 | 1×2.76 mm solid | 1 | 4.8 | 57.6 | 74.8 | 19 | Standard H07G-U configurations
| H07G-U 1×10 | 10 | 1×3.57 mm solid | 1.2 | 6 | 96 | 121.9 | 24 | Standard H07G-U configurations
| H07G-U 1×16 | 16 | 1×4.51 mm solid | 1.2 | 7 | 153.6 | 185.3 | 28 | Standard H07G-U configurations
Outer diameters and weights are nominal engineering values for H07G-U subject to standard manufacturing tolerances per EN 50525-2-42 / DIN VDE 0285-525-2-42.

## Electrical & rating data
H07G-U Solid-Conductor EVA Heat-Resistant Wire – Electrical & rating data (9)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-u-solid-conductor-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Configuration | Max. DC R @ 20 °C Ω/km | Primary rating (A or kV) | Derated / AC rating | Dielectric test V AC rms
1×0.5 mm² | 36.7 | 12 | 9 | 2500
1×0.75 mm² | 24.8 | 16 | 12 | 2500
1×1 mm² | 18.2 | 20 | 15 | 2500
1×1.5 mm² | 12.2 | 26 | 20 | 2500
1×2.5 mm² | 7.56 | 36 | 28 | 2500
1×4 mm² | 4.7 | 49 | 37 | 2500
1×6 mm² | 3.11 | 63 | 48 | 2500
1×10 mm² | 1.84 | 86 | 66 | 2500
1×16 mm² | 1.16 | 115 | 88 | 2500
Electrical resistance at +20 °C and dielectric withstand voltages verified per EN 50525-2-42 / DIN VDE 0285-525-2-42.

## Technical data
H07G-U Solid-Conductor EVA Heat-Resistant Wire – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-u-solid-conductor-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (U0/U · 2500 V AC test voltage)
Key data | Max temperature | +110 °C (Continuous conductor · +120 °C peak)
Key data | Conductor | Sn-Cu Class 1 (Solid tinned copper per IEC 60228)
Key data | Insulation | EVA Type EI3 (Cross-linked elastomer EN 50363-1)
Key data | Min bend radius | 4 × OD fixed (≤ 8 mm OD (5 × OD > 8 mm))
Key data | Size range | 1.5 to 10 mm² (Harmonised + 0.5–16 mm² extended)
Electrical | Rated voltage U0/U | 450/750 V AC
Electrical | Protected switchgear voltage | Up to 600/1000 V AC in protected ducts
Electrical | AC test voltage | 2500 V AC (50 Hz, 5 min)
Electrical | Insulation resistance (20 °C) | ≥ 200 MΩ·km (≥ 0.011 MΩ·km at +110 °C)
Electrical | Current rating basis | DIN VDE 0298-4 for +110 °C heat-resistant wire
Thermal | Continuous conductor temp. | -40 °C to +110 °C
Thermal | Short-term peak temperature | +120 °C (up to 1000 h cumulative)
Thermal | Max. short-circuit temperature | +250 °C (max. 5 s duration)
Thermal | Min. installation temperature | -25 °C during handling and bending
Mechanical | Conductor stranding class | IEC 60228 Class 1 (solid single wire)
Mechanical | Min. bending radius (≤ 8 mm OD) | 4 × overall diameter (fixed installation)
Mechanical | Min. bending radius (> 8 mm OD) | 5 × overall diameter (fixed installation)
Mechanical | Max. pulling tension | 50 N/mm² of copper cross-section (static)
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2 vertical flame
Resistance | Halogen-free & acid gas | IEC 60754-1 / EN 60754-2 (pH ≥ 4.3)
Resistance | Smoke density | Low smoke emission per IEC 61034-2
Resistance | Thermal ageing & ozone | Cross-linked EI3 resists ozone & UV
Standards | Construction standard | EN 50525-2-42 / DIN VDE 0285-525-2-42
Standards | Former national code | HD 22.7 S2 / DIN VDE 0282-7
Standards | Conductor specification | IEC 60228 / DIN EN 60228 Class 1 tinned
Standards | RoHS & REACH | 2011/65/EU (RoHS 3) & REACH SVHC compliant
Identification | Insulation colours | Black, blue, brown, red, white, grey, GNYE
Identification | Surface legend | TEBAOFLEX H07G-U <HAR> [mm²] EN 50525-2-42
Identification | Customs tariff (HS) | 8544.49

## Construction
H07G-U Solid-Conductor EVA Heat-Resistant Wire – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-u-solid-conductor-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid tinned copper conductor | Tinned annealed electrolytic copper wire (Cu-ETP1, IEC 60228 Class 1)
2 | Primary EVA dielectric | Cross-linked ethylene-vinyl acetate (EVA) elastomer compound Type EI3
3 | Integral halogen-free outer skin | Homogeneous extruded EI3 EVA surface (colour-coded)
| H07G-U (1.5–10 mm²) | Harmonised EN 50525-2-42 solid Class 1 sizes in black, blue, brown, red, white, and green-yellow
| 05G-U (0.5–1.0 mm²) | Extended 300/500 V solid EVA hook-up gauges for compact luminaire ballasts and thermostat blocks

## Quality and supply
H07G-U Solid-Conductor EVA Heat-Resistant Wire – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07g-u-solid-conductor-eva-heat-resistant-wire/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-2-42 / DIN VDE 0285-525-2-42. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Dielectric spark / high-voltage withstand test — 100 % in-line spark and AC/DC dielectric withstand per EN 50525-2-42 / DIN VDE 0285-525-2-42 | Every manufactured length
Routine test | Conductor DC resistance & continuity check — Within maximum 20 °C resistance limit specified for H07G-U | Every spool or drum length
Sample test | Thermal ageing & dimensional verification — Wall thickness, concentricity and post-ageing elongation per EN 50525-2-42 / DIN VDE 0285-525-2-42 | Per production batch
Type test | Flame, outgassing or high-temperature endurance — Qualified to EN 50525-2-42 / DIN VDE 0285-525-2-42 thermal and environmental performance criteria | Type qualification
Standard / approval | EN 50525-2-42 / DIN VDE 0285-525-2-42
Standard / approval | CE (2014/35/EU) & RoHS 3 (2015/863/EU) Compliant
Standard / approval | REACH SVHC & Halogen/Asbestos Compliance Verified
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H07G-U 450/750 V 1×2.5 EN 50525-2-42 CE
Supply | Delivery form: Precision spools, coils or export wooden drums
Supply | Standard lengths: 50 m · 100 m · 500 m · 1000 m (or cut harnesses)
Supply | MOQ: 100 m (stock sizes) · 300–500 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP