## Request a quote
Request a quotation for H07ZZ-F
Application engineer · LSZH & fire-performance cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h07zz-f-halogen-free-rubber-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H07ZZ-F Halogen-Free Rubber Cable – Dimensions & weights (23)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07zz-f-halogen-free-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-3-21 (HD 22.13). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| H07ZZ-F 1×16 | 1×16 | 6 | 9.9 | 10.8 | 154 | 240 | 43 | Single-core H07ZZ-F LSZH power & UPS loadbank leads (16–240 mm²)
| H07ZZ-F 1×35 | 1×35 | 2 | 13.2 | 14.3 | 336 | 455 | 57 | Single-core H07ZZ-F LSZH power & UPS loadbank leads (16–240 mm²)
| H07ZZ-F 1×50 | 1×50 | 1 | 15.2 | 16.5 | 480 | 635 | 66 | Single-core H07ZZ-F LSZH power & UPS loadbank leads (16–240 mm²)
| H07ZZ-F 1×70 | 1×70 | 2/0 | 17.1 | 18.6 | 672 | 850 | 74 | Single-core H07ZZ-F LSZH power & UPS loadbank leads (16–240 mm²)
| H07ZZ-F 1×95 | 1×95 | 3/0 | 19.3 | 21 | 912 | 1130 | 84 | Single-core H07ZZ-F LSZH power & UPS loadbank leads (16–240 mm²)
| H07ZZ-F 1×120 | 1×120 | 4/0 | 21.3 | 23.2 | 1152 | 1405 | 93 | Single-core H07ZZ-F LSZH power & UPS loadbank leads (16–240 mm²)
| H07ZZ-F 1×185 | 1×185 | 350 kcmil | 25.8 | 28 | 1776 | 2095 | 112 | Single-core H07ZZ-F LSZH power & UPS loadbank leads (16–240 mm²)
| H07ZZ-F 1×240 | 1×240 | 500 kcmil | 29 | 31.5 | 2304 | 2690 | 126 | Single-core H07ZZ-F LSZH power & UPS loadbank leads (16–240 mm²)
| H07ZZ-F 3G1.5 | 3G1.5 | 16 | 9 | 9.8 | 43 | 138 | 39 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G1.5 | 4G1.5 | 16 | 9.9 | 10.8 | 58 | 172 | 43 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 5G1.5 | 5G1.5 | 16 | 10.9 | 11.9 | 72 | 210 | 48 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 3G2.5 | 3G2.5 | 14 | 10.7 | 11.6 | 72 | 202 | 46 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G2.5 | 4G2.5 | 14 | 11.8 | 12.8 | 96 | 250 | 51 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 5G2.5 | 5G2.5 | 14 | 13.1 | 14.2 | 120 | 312 | 57 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G4 | 4G4 | 12 | 13.6 | 14.8 | 154 | 362 | 59 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 5G4 | 5G4 | 12 | 15.1 | 16.4 | 192 | 446 | 66 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G6 | 4G6 | 10 | 15.5 | 16.8 | 230 | 495 | 67 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 5G6 | 5G6 | 10 | 17.3 | 18.8 | 288 | 610 | 75 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G10 | 4G10 | 8 | 20.1 | 21.8 | 384 | 860 | 87 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G16 | 4G16 | 6 | 23.2 | 25.2 | 614 | 1210 | 101 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G25 | 4G25 | 4 | 28 | 30.4 | 960 | 1790 | 122 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G35 | 4G35 | 2 | 31.5 | 34.2 | 1344 | 2360 | 137 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
| H07ZZ-F 4G50 | 4G50 | 1 | 36.4 | 39.6 | 1920 | 3250 | 158 | Multicore H07ZZ-F LSZH power & control cables (3G1.5–4G50)
Dimensions and weights are typical values per EN 50525-3-21 (HD 22.13). Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
H07ZZ-F Halogen-Free Rubber Cable – Electrical & current ratings (14)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07zz-f-halogen-free-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-3-21 (HD 22.13). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | 1-core in air 30 °C, A | 3–4 core in air 30 °C, A
1.5 | 16 | 13.3 | 23 | 18
2.5 | 14 | 7.98 | 30 | 25
4 | 12 | 4.95 | 41 | 34
6 | 10 | 3.3 | 53 | 44
10 | 8 | 1.91 | 74 | 61
16 | 6 | 1.21 | 99 | 82
25 | 4 | 0.78 | 131 | 108
35 | 2 | 0.554 | 162 | 135
50 | 1 | 0.386 | 202 | 168
70 | 2/0 | 0.272 | 250 | 207
95 | 3/0 | 0.206 | 301 | 250
120 | 4/0 | 0.161 | 352 | 292
185 | 350 kcmil | 0.106 | 461 | 382
240 | 500 kcmil | 0.08 | 540 | 453
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / EN 50565-1. Apply derating factors for elevated ambient temperature or reeling layer grouping.

## Technical data
H07ZZ-F Halogen-Free Rubber Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07zz-f-halogen-free-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-3-21 (HD 22.13). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 450/750 V (0.6/1 kV fixed protected · 2.5 kV test)
Key data | Conductor temp. | +90 °C max. (+250 °C short-circuit (5 s))
Key data | Ambient temp. | −5…+70 °C (Flexing (−40…+70 °C fixed))
Key data | Bending radius | 4–8 × OD (4–6 × OD fixed · 6–8 × OD flexing)
Key data | Fire & smoke | IEC 60332-3-24 (Bunched flame + IEC 60754 / 61034)
Key data | Size range | 1.5–240 mm² (1 to 12 cores · EI8/EM8 LSZH)
Electrical | Rated voltage U0/U | 450/750 V AC (0.6/1 kV fixed protected)
Electrical | Max. operating voltage | 495/825 V AC (up to 1000 V AC protected)
Electrical | AC test voltage | 2500 V AC (50 Hz, 15 min)
Electrical | Conductor stranding | IEC 60228 Class 5 fine-stranded bare copper
Electrical | Current rating basis | DIN VDE 0298-4 (+90 °C conductor rating)
Thermal | Max. conductor temperature | +90 °C continuous operation
Thermal | Short-circuit temperature | +250 °C max. (up to 5 s)
Thermal | Temperature, flexing | −5 °C to +70 °C
Thermal | Temperature, fixed | −40 °C to +70 °C
Mechanical | Min. bending radius, fixed | 4 × OD (OD ≤ 25 mm) · 6 × OD (OD > 25 mm)
Mechanical | Min. bending radius, moving | 6 × OD (OD ≤ 25 mm) · 8 × OD (OD > 25 mm)
Mechanical | Max. tensile load | 15 N/mm² dynamic (50 N/mm² static)
Mechanical | Mechanical duty class | Medium-to-heavy mechanical stress (EN 50565-2)
Resistance | Halogen-free / acid gas | EN 60754-1 & EN 60754-2 (pH ≥ 4.3, conductivity ≤ 10 µS/mm)
Resistance | Smoke density | EN 61034-2 / IEC 61034-2 (light transmittance ≥ 60 %)
Resistance | Flame propagation | EN 60332-1-2 single & EN 60332-3-24 Cat. C bunched flame
Resistance | Oil & ozone resistance | EN 60811-404 oil & EN 60811-403 ozone resistant (EM8)
Standards | Construction standard | EN 50525-3-21 (HD 22.13 S2 / DIN VDE 0285-525-3-21)
Standards | Compound standards | EN 50363-5 Type EI8 & EN 50363-6 Type EM8
Standards | Selection & installation | EN 50565-1 & EN 50565-2
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Black
Identification | Core identification | HD 308 S2 colour code (≤ 5 cores); black numbered + GN/YE (≥ 6 cores)
Identification | Sheath marking | TEBAOFLEX H07ZZ-F <HAR> [Size] 450/750V EN 50525-3-21 LSZH CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
H07ZZ-F Halogen-Free Rubber Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07zz-f-halogen-free-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-3-21 (HD 22.13). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible copper conductor | Fine-stranded bare copper wire (IEC 60228 Class 5) | EN 60228 Class 5
2 | Separator tape | Halogen-free polyester foil separator over conductor on larger sizes
3 | LSZH elastomer insulation | Cross-linked halogen-free low-smoke elastomeric compound Type EI8 (+90 °C) | EN 50363-5 EI8
4 | LSZH elastomer outer sheath | Cross-linked halogen-free, low-smoke, flame-retardant elastomeric compound Type EM8, black | EN 50363-6 EM8 · IEC 60754-2 & IEC 61034-2
| H07ZZ-F Single-Core (1×1.5–1×240) | Halogen-free single-core flexible power tails for UPS, data centre loadbanks and switchgear
| H07ZZ-F Multicore (2–12C, 1.5–50) | Halogen-free multi-core flexible power and control cables with HD 308 S2 colour or numbered cores

## Quality and supply
H07ZZ-F Halogen-Free Rubber Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h07zz-f-halogen-free-rubber-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50525-3-21 (HD 22.13). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.5 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 Class 5 (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath elastomer physical properties — EN 50525-3-21 (HD 22.13) | Type approval
Standard / approval | EN 50525-3-21 (HD 22.13)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H07ZZ-F 450/750 V [Size] EN 50525-3-21 LSZH CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pilot cores or sheath colours on request