## Request a quote
Request a quotation for H1Z2Z2-K
Specify conductor cross-section or AWG, core count, voltage class and drum/reel length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/h1z2z2-k-solar-pv-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
H1Z2Z2-K Solar PV Cable – Dimensions & masses (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h1z2z2-k-solar-pv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50618 / IEC 62930 / TÜV 2 PfG 1169. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cross-Section | Insul / Sheath mm | Nom. OD mm | Copper kg/km | Total mass ≈ kg/km | Min. bend R mm | Series
| H1Z2Z2-K 1×1.5 | 1 × 1.5 mm² | 0.7 / 0.8 mm | 4.6 | 14.4 | 34 | 18.4 | H1Z2Z2-K size schedule
| H1Z2Z2-K 1×2.5 | 1 × 2.5 mm² | 0.7 / 0.8 mm | 5 | 24 | 46 | 20 | H1Z2Z2-K size schedule
| H1Z2Z2-K 1×4.0 | 1 × 4.0 mm² | 0.7 / 0.8 mm | 5.6 | 38.4 | 62 | 22.4 | H1Z2Z2-K size schedule
| H1Z2Z2-K 1×6.0 | 1 × 6.0 mm² | 0.7 / 0.8 mm | 6.2 | 57.6 | 84 | 24.8 | H1Z2Z2-K size schedule
| H1Z2Z2-K 1×10 | 1 × 10 mm² | 0.7 / 0.8 mm | 7.4 | 96 | 130 | 29.6 | H1Z2Z2-K size schedule
| H1Z2Z2-K 1×16 | 1 × 16 mm² | 0.7 / 0.9 mm | 8.8 | 153.6 | 198 | 35.2 | H1Z2Z2-K size schedule
| H1Z2Z2-K 1×25 | 1 × 25 mm² | 0.9 / 1.0 mm | 10.8 | 240 | 305 | 43.2 | H1Z2Z2-K size schedule
| H1Z2Z2-K 1×35 | 1 × 35 mm² | 0.9 / 1.1 mm | 12.2 | 336 | 415 | 48.8 | H1Z2Z2-K size schedule
Dimensions and tolerances conform to EN 50618 / IEC 62930 / TÜV 2 PfG 1169.

## Electrical data
H1Z2Z2-K Solar PV Cable – Electrical data (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/h1z2z2-k-solar-pv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50618 / IEC 62930 / TÜV 2 PfG 1169. Values for your order are confirmed in the quotation.
Cross-Section | Max. DC R @ 20 °C Ω/km | Current in air A | Installed / duty A
1 × 1.5 mm² | 13.7 | 30 | 24
1 × 2.5 mm² | 8.21 | 41 | 33
1 × 4.0 mm² | 5.09 | 55 | 44
1 × 6.0 mm² | 3.39 | 70 | 56
1 × 10 mm² | 1.95 | 98 | 78
1 × 16 mm² | 1.24 | 132 | 106
1 × 25 mm² | 0.795 | 176 | 141
1 × 35 mm² | 0.565 | 218 | 174
Reference ampacities at +30 °C ambient; apply duty-cycle or grouping correction factors per standard.

## Technical data
H1Z2Z2-K Solar PV Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/h1z2z2-k-solar-pv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50618 / IEC 62930 / TÜV 2 PfG 1169. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | DC voltage rating | 1.5 / 1.5 kV DC (1.8 kV DC max. system voltage)
Key data | AC voltage rating | 1.0 / 1.0 kV AC (1.2 kV AC max. operating)
Key data | Conductor | Class 5 tinned C (EN 60228 corrosion-proof strands)
Key data | Insulation & sheat | Dual cross-linke (E-beam cross-linked LSZH polyolefin)
Key data | Thermal endurance | -40 to +90 / +12 (20,000 h @ +120 °C · +250 °C SC)
Key data | Size range | 1.5 to 35 mm² (Module leads to combiner feeders)
Electrical | Nominal DC voltage (U0/U) | 1.5 / 1.5 kV DC (max. permitted operating voltage 1.8 kV DC)
Electrical | Nominal AC voltage (U0/U) | 1.0 / 1.0 kV AC (1.2 kV AC max.)
Electrical | Test voltage (5 min water bath) | 6.5 kV AC rms or 15 kV DC
Thermal | Ambient & conductor temperature | -40 °C to +90 °C continuous · +120 °C max conductor temp (20,000 h)
Thermal | Short-circuit temperature (5 s) | +250 °C (thermoset e-beam cross-linked Z2)
Thermal | Expected service lifetime | ≥25 years per EN 50618 Arrhenius thermal endurance index
Mechanical | Minimum bending radius | 4 × D (fixed installation) · 5 × D (during flexing/tracker motion)
Mechanical | Dynamic penetration & shrinkage | Passes EN 50618 spring-steel needle penetration & ≤2 % longitudinal shrinkage
Resistance | Weathering, UV & ozone | 720 h Xenon-arc UV + water spray (EN 50289-4-17) & ozone EN 50396 Method B
Resistance | Water immersion & ammonia | AD7 / AD8 long-term DC water stability (UL 44 / EN 50618) & agricultural ammonia resistant
Resistance | Fire, smoke & halogen emission | IEC 60332-1-2 flame, IEC 61034-2 (≥70 % light), EN 50525-1 Annex B halogen-free
Standards | Governing standards | BS EN 50618:2014 & IEC 62930 (62930 IEC 131)
Standards | Legacy compatibility | Fully backward-compatible with 1000 V DC TÜV 2 PfG 1169 / PV1-F systems
Identification | CENELEC designation | H = harmonized · 1 = 1.0 kV AC / 1.5 kV DC · Z2 = cross-linked LSZH insulation · Z2 = cross-linked LSZH sheath · -K = Class 5 flexible
Identification | Sheath colours | Black, Red, or Blue

## Construction
H1Z2Z2-K Solar PV Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/h1z2z2-k-solar-pv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50618 / IEC 62930 / TÜV 2 PfG 1169. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 tinned copper (EN 60228) | Fine-stranded tin-coated annealed copper conductor resisting galvanic and humid salt-mist corrosion over 25+ years | EN 60228
2 | Cross-linked LSZH polyolefin (Z2) | Electron-beam cross-linked halogen-free inner insulation (≥0.7–1.0 mm wall) providing Class II double insulation | EN 50618
3 | UV/ozone cross-linked LSZH jacket (Z2) | Weather-, ammonia-, acid/alkali- and hydrolysis-resistant cross-linked polyolefin outer sheath (Black, Red or Blue) | EN 50618
| H1Z2Z2-K Black Outer Sheath (RAL 9005) | Carbon-black UV-stabilised outer sheath over white cross-linked inner insulation for negative/universal PV string runs.
| H1Z2Z2-K Red (RAL 3000) / Blue Polarity | UV-stabilised red (DC+) or blue (DC−) outer sheath for visual polarity verification at combiner boxes and MPPT inputs.

## Quality and supply
H1Z2Z2-K Solar PV Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/h1z2z2-k-solar-pv-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50618 / IEC 62930 / TÜV 2 PfG 1169. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 6.5 kV AC / 15 kV DC water-bath test & spark test — Zero breakdown; tinned Cu resistance per EN 60228 Class 5 | 100 % of drums
Sample test | Hot-set cross-linking, longitudinal shrinkage & cold impact — Hot-set ≤175 %; shrinkage ≤2 %; -40 °C cold impact pass | Every batch
Type test | 20,000-hour +120 °C Arrhenius thermal index & 720-hour UV — Certified to BS EN 50618 & IEC 62930 | Type qualification
Standard / approval | BS EN 50618 (H1Z2Z2-K)
Standard / approval | IEC 62930 (62930 IEC 131)
Standard / approval | TÜV Rheinland / VDE Certified
Standard / approval | CPR EN 50575 Dca-s2,d2,a1
Standard / approval | RoHS 3 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX H1Z2Z2-K 1x[size]mm2 EN 50618 1.5kV DC IEC 62930 131 HAL-FREE [lot/m]
Supply | Delivery form: Non-returnable wooden drums, export reels or shrink-wrapped coils
Supply | Standard drum lengths: 100 m · 250 m · 500 m · 1000 m
Supply | MOQ: 200 m (stock sizes) · 500 m (custom lengths)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP