## Request a quote
Request a quotation for HSUS / HSL
High-voltage coaxial cable engineer
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/screened-silicone-high-voltage-connection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
HSUS / HSL Screened Silicone High-Voltage Connection Cable – Voltage ratings, coaxial diameters & capacitance (12)
TEBAOFLEX ¦ https://tebaoflex.com/cables/screened-silicone-high-voltage-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60502-2 / IEC 60270 / VDE 0250. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Conductor mm² (AWG) | Rated U_DC kV DC | Test U_DC kV DC | Dielectric OD mm | Overall OD mm | Capacitance pF/m | Weight kg/km | Series
| HSUS-10KV-1.0 | 1.0 (18 AWG) | 10 | 20 | 3.8 | 6.2 | 155 | 58 | HSUS Series — Silicone HV Core + Tough PVC/PUR Outer Sheath (10–100 kV DC)
| HSUS-20KV-1.5 | 1.5 (16 AWG) | 20 | 40 | 5.2 | 7.8 | 135 | 88 | HSUS Series — Silicone HV Core + Tough PVC/PUR Outer Sheath (10–100 kV DC)
| HSUS-30KV-1.5 | 1.5 (16 AWG) | 30 | 55 | 6.6 | 9.4 | 118 | 124 | HSUS Series — Silicone HV Core + Tough PVC/PUR Outer Sheath (10–100 kV DC)
| HSUS-40KV-2.5 | 2.5 (14 AWG) | 40 | 70 | 8 | 11 | 122 | 168 | HSUS Series — Silicone HV Core + Tough PVC/PUR Outer Sheath (10–100 kV DC)
| HSUS-50KV-2.5 | 2.5 (14 AWG) | 50 | 85 | 9.4 | 12.6 | 110 | 215 | HSUS Series — Silicone HV Core + Tough PVC/PUR Outer Sheath (10–100 kV DC)
| HSUS-65KV-2.5 | 2.5 (14 AWG) | 65 | 110 | 11.2 | 14.8 | 102 | 285 | HSUS Series — Silicone HV Core + Tough PVC/PUR Outer Sheath (10–100 kV DC)
| HSUS-100KV-4.0 | 4.0 (12 AWG) | 100 | 160 | 15.8 | 19.8 | 96 | 490 | HSUS Series — Silicone HV Core + Tough PVC/PUR Outer Sheath (10–100 kV DC)
| HSL-15KV-1.5-SIR | 1.5 (16 AWG) | 15 | 30 | 4.6 | 7.2 | 145 | 76 | HSL Series — All-Silicone −60/+180 °C Screened HV Cable (15–100 kV DC)
| HSL-30KV-1.5-SIR | 1.5 (16 AWG) | 30 | 55 | 6.6 | 9.6 | 118 | 128 | HSL Series — All-Silicone −60/+180 °C Screened HV Cable (15–100 kV DC)
| HSL-50KV-2.5-SIR | 2.5 (14 AWG) | 50 | 85 | 9.4 | 12.8 | 110 | 220 | HSL Series — All-Silicone −60/+180 °C Screened HV Cable (15–100 kV DC)
| HSL-75KV-2.5-SIR | 2.5 (14 AWG) | 75 | 125 | 12.6 | 16.4 | 98 | 345 | HSL Series — All-Silicone −60/+180 °C Screened HV Cable (15–100 kV DC)
| HSL-100KV-6.0-SIR | 6.0 (10 AWG) | 100 | 160 | 16.5 | 20.8 | 105 | 545 | HSL Series — All-Silicone −60/+180 °C Screened HV Cable (15–100 kV DC)
When terminating HSUS / HSL cables, always strip back the outer semiconductive layer cleanly to the manufacturer stress-cone dimension so it does not bridge the HV termination creepage path.

## Technical data
HSUS / HSL Screened Silicone High-Voltage Connection Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/screened-silicone-high-voltage-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60502-2 / IEC 60270 / VDE 0250. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | DC voltage range | 10 to 100 kV DC (4 kV to 40 kV AC rms (50/60 Hz))
Key data | Field confinement | 100 % Touch-Safe (Grounded outer braid confines E-field)
Key data | Stress grading | Dual Semicon (Inner & outer semiconductive layers)
Key data | HSUS vs HSL | 2 Outer Sheaths (HSUS: PVC/PUR · HSL: −60/+180°C SiR)
Key data | Partial disch. | ≤ 5 pC @ 1.2 U0 (Corona-free coaxial geometry)
Key data | Bend radius | 6 × OD (Supple coaxial laboratory & rack routing)
Electrical | Rated DC working voltage | 10, 15, 20, 30, 40, 50, 60, 75 & 100 kV DC
Electrical | Rated AC voltage (50/60 Hz) | 4 kV to 40 kV AC rms
Electrical | Factory DC routine test | 1.5 × to 2.0 × rated U_DC (core to screen) for 5 min
Electrical | Jacket spark / dielectric test | 3.0 kV AC rms on outer sheath
Electrical | Nominal capacitance | 95 pF/m to 180 pF/m (size & voltage dependent)
Electrical | Partial discharge level | ≤ 5 pC at 1.2 × rated U_AC rms (IEC 60270)
Thermal | Operating temperature (HSUS) | −25 °C to +80 °C (PVC) · −40 °C to +90 °C (PUR)
Thermal | Operating temperature (HSL) | −60 °C to +180 °C (all-silicone)
Mechanical | Center conductor sizes | 0.75, 1.0, 1.5, 2.5, 4.0, 6.0, 10 & 16 mm²
Mechanical | Min. bend radius | 6 × OD static · 10 × OD flexing
Resistance | Touch safety | Fully grounded concentric screen (EN 50191 / IEC 61010)
Resistance | Flame retardancy | IEC 60332-1-2 · HSL zero-halogen IEC 60754-1
Standards | Design & test standards | IEC 60502-2 · IEC 60270 · DIN VDE 0250
Standards | HV connector compatibility | Redel-HV Redel/HV, HV-Lock, OEM, HV-Plug & Claymount HV plugs
Identification | Outer sheath colour | Red (RAL 3000/3013), Grey (RAL 7001) or Black
Identification | Surface legend | TEBAOFLEX HSUS / HSL SCREENED HV CABLE [kV DC]
Identification | Customs tariff (HS) | 8544.60

## Construction
HSUS / HSL Screened Silicone High-Voltage Connection Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/screened-silicone-high-voltage-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60502-2 / IEC 60270 / VDE 0250. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Fine-stranded tinned copper HV center conductor | Stranded tinned copper (IEC 60228 Class 5, 0.75 mm² / 19 AWG to 16 mm² / 6 AWG)
2 | Inner semiconductive silicone stress-smoothing layer | Co-extruded semiconductive silicone layer bonded over the center conductor
3 | Void-free high-voltage silicone rubber dielectric | High-purity vacuum-extruded silicone rubber (≥ 30 kV/mm breakdown strength) | Provides flexible 10 kV to 100 kV DC insulation
4 | Outer semiconductive silicone screen | Extruded semiconductive silicone layer (or conductive tape) under the metallic braid
5 | ≥ 85 % tinned copper braided earth shield | Concentric tinned copper wire braid (≥ 85 % optical coverage)
6 | HSUS (PVC/PUR) or HSL (Silicone) outer sheath | HSUS: flame-retardant red/grey/black PVC or PUR (−25 to +80/+90 °C) · HSL: cross-linked silicone rubber (−60 to +180 °C)
| HSUS (Silicone HV Core + PVC / PUR Outer Sheath) | Tough, abrasion- and oil-resistant PVC or PUR outer jacket (−25 °C to +90 °C) for HV power supply output cables and industrial racks
| HSL (All-Silicone Core + Silicone Outer Sheath, +180 °C) | Ultra-limp all-silicone construction rated −60 °C to +180 °C with halogen-free flame retardancy for thermal chambers and scientific systems

## Quality and supply
HSUS / HSL Screened Silicone High-Voltage Connection Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/screened-silicone-high-voltage-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60502-2 / IEC 60270 / VDE 0250. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Core-to-screen DC high-voltage proof test — 20 kV DC to 160 kV DC applied between center conductor and grounded copper braid for 5 min | 100 % of finished reels
Routine test | Partial discharge measurement (IEC 60270) — PD ≤ 5 pC at 1.2 × rated AC rms voltage | Every production length ≥ 20 kV
Sample test | Outer sheath 3 kV AC dielectric & transfer impedance check — Verify outer jacket isolation and ≥ 85 % braid coverage | Production lot
Standard / approval | IEC 60270 Partial-Discharge Tested (≤ 5 pC)
Standard / approval | DIN VDE 0250 & EN 50191 Touch-Safe Screened HV
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX HSUS / HSL SCREENED HIGH VOLTAGE CABLE [kV DC]
Supply | Delivery form: 50 m / 100 m / 250 m reels or pre-terminated HV plug assemblies
Supply | Termination service: Factory-moulded HV silicone stress cones & coaxial HV connectors
Supply | Quality report: Individual DC hipot & IEC 60270 partial-discharge test certificate
Supply | Lead time: 2–4 weeks ex-works