## Request a quote
Request a quotation for Hybrid Fibre-Copper Microcable
Application engineer · optical & sensing cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/siroccohybrid-composite-fibre-optic-and-copper-power-air-blown-microcable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
Composite Fibre-Optic and Copper Power Air-Blown Microcable – Dimensions, DC resistance & duct fit (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/siroccohybrid-composite-fibre-optic-and-copper-power-air-blown-microcable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 60794-5-10 / IEC 60228 / ITU-T G.657.A1. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Copper + optical compliment | Outer Ø mm | Weight ≈ kg/km | Cu DC R Ω/km | Min. duct ID mm | Series
| Hybrid Fibre-Copper Microcable 2×0.5+04F | 2 × 0.50 mm² Cu + 4F G.657.A1 | 4.8 | 28 | 39 | 8 | Composite Copper Power + G.657.A1 Optical Microcables
| Hybrid Fibre-Copper Microcable 2×0.75+12F | 2 × 0.75 mm² Cu + 12F G.657.A1 | 5.5 | 38 | 26 | 8 | Composite Copper Power + G.657.A1 Optical Microcables
| Hybrid Fibre-Copper Microcable 2×1.5+12F | 2 × 1.50 mm² Cu + 12F G.657.A1 | 6.4 | 56 | 13.3 | 10 | Composite Copper Power + G.657.A1 Optical Microcables
| Hybrid Fibre-Copper Microcable 2×2.5+12F | 2 × 2.50 mm² Cu + 12F G.657.A1 | 7.5 | 82 | 7.98 | 10 | Composite Copper Power + G.657.A1 Optical Microcables
| Hybrid Fibre-Copper Microcable 2×2.5+24F | 2 × 2.50 mm² Cu + 24F G.657.A1 | 7.8 | 88 | 7.98 | 12 | Composite Copper Power + G.657.A1 Optical Microcables
At 56 V DC remote feed, 2 × 2.5 mm² delivers 100 W at up to 450 m or 60 W at up to 750 m.

## Technical data
Composite Fibre-Optic and Copper Power Air-Blown Microcable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/siroccohybrid-composite-fibre-optic-and-copper-power-air-blown-microcable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 60794-5-10 / IEC 60228 / ITU-T G.657.A1. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Optical cores | 2 to 24 fibres (ITU-T G.657.A1 bend-insensitive)
Key data | Copper power | 2 × 0.5–2.5 mm² (IEC 60228 Class 5 annealed Cu)
Key data | Voltage rating | 300 V DC / AC (48–60 V SELV / RFT / PoE+)
Key data | Outer Ø | 4.8 to 7.8 mm (Fits 8/6, 10/8 & 12/10 mm ducts)
Key data | Blowing reach | Up to 1,200 m (Low-friction microduct sheath)
Key data | Temperature | -30 to +70 °C (Continuous remote powering)
Electrical | Copper cross-sections | 2 × 0.50 mm² · 2 × 0.75 mm² · 2 × 1.50 mm² · 2 × 2.50 mm²
Electrical | Max. DC resistance @ 20 °C | 39.0 Ω/km (0.5) · 26.0 Ω/km (0.75) · 13.3 Ω/km (1.5) · 7.98 Ω/km (2.5)
Electrical | Nominal voltage rating | 300 V DC / AC rms (48 V SELV / ±190 V RFT Class 2)
Electrical | Dielectric test voltage | 1,500 V AC rms for 1 min
Thermal | Operating temperature | -30 °C to +70 °C
Thermal | Installation (blowing) temp. | -10 °C to +50 °C
Thermal | Storage temperature | -40 °C to +70 °C
Mechanical | Outer diameter range | 4.8 mm (2×0.5 + 4F) to 7.8 mm (2×2.5 + 24F)
Mechanical | Max. pulling / blowing load | 600 N to 1,400 N
Mechanical | Crush resistance | 1,000 N / 100 mm
Mechanical | Min. bend radius | 15 × OD (static) · 20 × OD (installation)
Optical | Optical fibre type | ITU-T G.657.A1 bend-insensitive SM (2 to 24 fibres)
Optical | Attenuation @ 1310 / 1550 nm | ≤ 0.35 dB/km @ 1310 nm · ≤ 0.21 dB/km @ 1550 nm
Optical | Macro-bend loss | ≤ 0.2 dB (10 turns @ R = 15 mm, 1550 nm)
Resistance | Water penetration | IEC 60794-1-22 Method F5B pass
Resistance | Flame option (LSZH) | IEC 60332-1-2 & IEC 60332-3-24 Cat C
Resistance | Microduct blowing | Up to 1,000–1,200 m per blowing shot
Standards | Microcable & conductor std | IEC 60794-5-10 & IEC 60228 Class 5
Standards | Remote power safety | IEC 62368-1 ES1/ES2 & NEC Class 2 compatible
Standards | RoHS & REACH | 2011/65/EU & EC 1907/2006 compliant
Identification | Power core colours | Blue (-) & Red (+) or Black & Red
Identification | Fibre colour code | TIA-598-D 12-colour
Identification | Customs tariff (HS) | 8544.7000

## Construction
Composite Fibre-Optic and Copper Power Air-Blown Microcable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/siroccohybrid-composite-fibre-optic-and-copper-power-air-blown-microcable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 60794-5-10 / IEC 60228 / ITU-T G.657.A1. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Copper power conductors + G.657.A1 optical fibres | 2 × 0.50, 0.75, 1.50 or 2.50 mm² Class 5 plain annealed copper conductors (IEC 60228) + 2 to 24 ITU-T G.657.A1 250/200 µm single-mode fibres
2 | Power core XLPE/PE insulation & optical micro-tube | Thin-wall high-dielectric PE/LSZH on copper conductors (Blue/Red or Black/Red) + gel-filled PBT optical loose micro-tube | 300 V rating & thermal isolation up to +70 °C
3 | Aramid / glass yarn & dry water-blocking bed | Longitudinal water-swellable yarns and non-metallic aramid/glass tensile elements
4 | Low-friction HDPE or flame-retardant LSZH sheath | Low-friction Black HDPE for outdoor microduct blowing or halogen-free LSZH (IEC 60332-3-24) for indoor/tunnel ducts
| Hybrid Fibre-Copper Microcable-HDPE (Outdoor Microduct) | Low-friction Black HDPE outer sheath for air-blowing up to 1,200 m in underground microducts
| Hybrid Fibre-Copper Microcable-LSZH (Indoor / Tunnel) | Halogen-free flame-retardant LSZH jacket for FTTB risers, airports, data centres and rail tunnels

## Quality and supply
Composite Fibre-Optic and Copper Power Air-Blown Microcable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/siroccohybrid-composite-fibre-optic-and-copper-power-air-blown-microcable/ ¦ Data revision 2026-10-21
Typical values for this cable type, based on IEC 60794-5-10 / IEC 60228 / ITU-T G.657.A1. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 100 % OTDR optical trace, conductor DC R & 1.5 kV AC test — Optical α ≤ 0.35/0.21 dB/km, DC R within IEC 60228, zero dielectric breakdown | Every manufactured drum length
Type test | Microduct blowing & tensile test (IEC 60794-1-21 E1 & E19) — ≥ 1,000 m air-blowing reach with zero optical or insulation damage | Type qualification
Type test | Combined current heating + thermal cycling test — Δα ≤ 0.05 dB/km under full rated DC load up to +70 °C | Type qualification
Standard / approval | IEC 60794-5-10 & IEC 60228
Standard / approval | ITU-T G.657.A1 & IEC 62368-1
Standard / approval | RoHS 2 & REACH Compliant
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX Hybrid Fibre-Copper Microcable 2x<MM2>Cu+<COUNT>F G.657.A1
Supply | Delivery form: Fumigated export wooden or steel drums
Supply | Standard drum lengths: 1000 m · 2000 m · 4000 m (or custom cut lengths)
Supply | MOQ: 500 m (standard) · 1000 m (custom build)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP