## Request a quote
Request a quotation for IEC 0.6/1 kV & UL WTTC 1000V Shielded
Share drive kW/voltage (0.6/1 kV, 1,000 V WTTC or 2,000 V RHW-2), 3+3 symmetrical or 4G cross-section, shield type (dual Cu tape or foil+braid) and total length.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/iec-0-6-1kv-ul-wttc-1000v-shielded-wind-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
IEC 0.6/1 kV & UL 2277 Type WTTC 1,000 V Copper-Braid Shielded Wind Tu – Dimensions, tensile load & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/iec-0-6-1kv-ul-wttc-1000v-shielded-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Net weight ≈ kg/km | Max. pulling kN ≈ | Min. bend R mm | Series
| IEC 0.6 4G16 / 3×16+3G2.5 | 4G16 mm² (or 3×6 AWG + 3G10 AWG) | IEC 60228 Class 5 / Class K Cu | 21.8 | 790 | 9.5 | 130 | IEC 0.6/1 kV & UL WTTC 1000V Shielded Construction Schedule (−40…+90 °C)
| IEC 0.6 4G50 / 3×50+3G10 | 4G50 mm² (or 3×1 AWG + 3G6 AWG) | IEC 60228 Class 5 / Class K Cu | 31.4 | 2140 | 22.5 | 190 | IEC 0.6/1 kV & UL WTTC 1000V Shielded Construction Schedule (−40…+90 °C)
| IEC 0.6 3×150+3G25 VFD | 3×150 + 3G25 mm² (or 3×350 kcmil) | IEC 60228 Class 5 / Class K Cu | 47.2 | 5480 | 58 | 285 | IEC 0.6/1 kV & UL WTTC 1000V Shielded Construction Schedule (−40…+90 °C)
Custom conductor cross-sections, core counts, pre-lugged tower kits and drum lengths available per UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification.

## Electrical & thermal parameters
IEC 0.6/1 kV & UL 2277 Type WTTC 1,000 V Copper-Braid Shielded Wind Tu – Electrical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/iec-0-6-1kv-ul-wttc-1000v-shielded-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ Ω/km | Rating / Impedance | Operating temp.
4G16 mm² (or 3×6 AWG + 3G10 AWG) | 1.15 | 0.6/1 kV / 1,000 V (98 A VFD) | −40…+90 °C
4G50 mm² (or 3×1 AWG + 3G6 AWG) | 0.387 | 0.6/1 kV / 1,000 V (195 A VFD) | −40…+90 °C
3×150 + 3G25 mm² (or 3×350 kcmil) | 0.129 | 0.6/1 kV / 1,000 V (395 A VFD) | −40…+90 °C
Every production length undergoes routine conductor DC resistance, AC high-voltage spark/dielectric and dimensional verification.

## Technical data
IEC 0.6/1 kV & UL 2277 Type WTTC 1,000 V Copper-Braid Shielded Wind Tu – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/iec-0-6-1kv-ul-wttc-1000v-shielded-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 0.6/1 kV / 1,000 (Tested per UL 2277 WTTC / IEC 60502-1)
Key data | Operating temp. | −40…+90 °C (Cold-climate & nacelle wind service)
Key data | Min. bend radius | 6 × OD (Drip-loop, hub & tower routing)
Key data | Core / conductor | IEC 60228 Class (Four flexible plain copper cores (3 phas)
Key data | Outer protection | Cold & Oil-Resis (Black flame-retardant thermoset elastome)
Key data | Standard | UL 2277 WTTC / I (UL Subject 2277 Type WTTC 1,000 V & IEC )
Electrical | Rated voltage / operating system | 0.6/1 kV / 1,000 V (UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification)
Electrical | Core / conductor construction | IEC 60228 Class 5 Flexible Copper (4G10 mm²) — Four flexible plain copper cores (3 phases + 1 green/yellow PE)
Electrical | Primary dielectric / insulation | EPR Dual-Standard Core Insulation — Ethylene-propylene rubber rated 0.6/1 kV IEC and 1,000 V UL WTTC
Thermal | Continuous operating temperature | −40…+90 °C (wind turbine nacelle, hub & tower duty)
Thermal | Low-temperature torsion & cold bend | Verified cold-flex and torsion endurance across −40…+90 °C per UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification
Thermal | Storage & transport temperature | −40…+80 °C on export wooden/steel cable drum
Mechanical | Outer jacket / sheath protection | Cold & Oil-Resistant Elastomer Jacket (-40 °C) — Black flame-retardant thermoset elastomer outer sheath
Mechanical | Minimum bending radius | 6 × OD
Mechanical | Intermediate screen / separator / core layer | Copper Wire Braid EMC Shield — Braided copper wire screen suppressing auxiliary VFD interference
Resistance | Oil, grease, ozone & UV resistance | Resistant to wind turbine gearbox oil, hydraulic fluid, ozone and UV weathering per UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification
Resistance | Flame retardancy & smoke/halogen emission | Flame-retardant and environmental performance verified per UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification
Standards | Conductor & flame/test standards | IEC 60228 / IEC 60332-1-2 & -3 / UL 2277 WTTC / EN 10204
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | IEC 0.6/1 kV & UL WTTC 1000V Shielded
Identification | Sheath colour & metre marking | Continuous metre-marked black outer finish (Cold & Oil-Resis)
Identification | Customs tariff (HS) | 8544.49 / 8544.60

## Construction
IEC 0.6/1 kV & UL 2277 Type WTTC 1,000 V Copper-Braid Shielded Wind Tu – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/iec-0-6-1kv-ul-wttc-1000v-shielded-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | IEC 60228 Class 5 Flexible Copper (4G10 | Four flexible plain copper cores (3 phases + 1 green/yellow PE)
2 | EPR Dual-Standard Core Insulation | Ethylene-propylene rubber rated 0.6/1 kV IEC and 1,000 V UL WTTC
3 | Copper Wire Braid EMC Shield | Braided copper wire screen suppressing auxiliary VFD interference
4 | Cold & Oil-Resistant Elastomer Jacket (- | Black flame-retardant thermoset elastomer outer sheath
| IEC 0.6/1 kV & UL WTTC 1000V Shielded — Standard Wind Turbine Execution | Built to UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification with iec 60228 class 5 flexible copper (4g10 mm²) and cold & oil-resistant elastomer jacket (-40 °c)
| IEC 0.6/1 kV & UL WTTC 1000V Shielded — Pre-Cut Tower / Drip-Loop Kit | Available on bulk export reels or pre-cut to turbine tower section and nacelle drip-loop lengths
| IEC 0.6/1 kV & UL WTTC 1000V Shielded — Cold Torsion & Routine Certified | Supplied with EN 10204 3.1 routine dielectric, conductor DC resistance & cold-torsion qualification report

## Quality and supply
IEC 0.6/1 kV & UL 2277 Type WTTC 1,000 V Copper-Braid Shielded Wind Tu – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/iec-0-6-1kv-ul-wttc-1000v-shielded-wind-cable/ ¦ Data revision 2026-10-27
Typical values for this cable type, based on UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & dimensional verification (UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification) — DC resistance at 20 °C and insulation/sheath wall thickness within UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification limits | Every manufactured drum length
Routine test | AC high-voltage dielectric & insulation resistance test (UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification) — Zero dielectric breakdown and verified insulation resistance for 0.6/1 kV / 1,000 V rating | Every manufactured drum length
Type test | Low-temperature drip-loop torsion, oil & flame qualification (UL Subject 2277 Type WTTC 1,000 V & IEC 60502-1 0.6/1 kV Shielded Wind Specification) — Verified cold torsion cycle endurance, oil resistance and flame retardancy across −40…+90 °C | Type qualification & periodic lot audit
Standard / approval | UL 2277 WTTC / IEC 60502-1 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX IEC 0.6/1 kV & UL WTTC 1000V Shielded UL 2277 WTTC / IEC 60502-1 0.6/1 kV / 1,000 V CE
Supply | Delivery form: Heavy-duty export fumigated wooden drums, steel reels or pre-cut wind turbine tower & drip-loop kits
Supply | Standard lengths: 500 m, 1,000 m or custom cut-to-length nacelle drip-loop and tower section sets
Supply | MOQ: 100 m (standard configurations) · 300 m (custom wind builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP