## Request a quote
Request a quotation for IEEE 1580 Type P
Specify the series (1C power, 3C power, 2 kV VFD or IS/OS shielded pairs), AWG/kcmil size, hazardous zone classification (Div 1 bronze-braid armoured vs Div 2 unarmoured) and required classification society certificates.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/ieee-1580-type-p-marine-offshore-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
IEEE 1580 Type P Marine & Offshore Drilling Cable – Dimensions & mass (79) (79)
TEBAOFLEX ¦ https://tebaoflex.com/cables/ieee-1580-type-p-marine-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / UL 1309 Type X110 / CSA C22.2 No. 245. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Designation | Cores × AWG / kcmil | Voltage grade | Stranding (No./AWG) | XLPO wall (mm) | Outer sheath (mm) | Nominal OD (in) | Nominal OD (mm) | Total mass (lb/kft) | Total mass (kg/km) | Series
| Type P 1×18 AWG 2 kV | 1 × 18 AWG (0.96 mm²) | 2 kV / 1 kV | 19/30 | 1.02 | 0 | 0.145 | 3.68 | 15 | 22 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×16 AWG 2 kV | 1 × 16 AWG (1.23 mm²) | 2 kV / 1 kV | 19/29 | 1.02 | 0 | 0.16 | 4.06 | 20 | 30 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×14 AWG 2 kV | 1 × 14 AWG (1.94 mm²) | 2 kV / 1 kV | 19/27 | 1.14 | 0 | 0.164 | 4.17 | 23 | 34 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×12 AWG 2 kV | 1 × 12 AWG (3.08 mm²) | 2 kV / 1 kV | 19/25 | 1.14 | 0 | 0.181 | 4.6 | 30 | 45 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×10 AWG 2 kV | 1 × 10 AWG (5.26 mm²) | 2 kV / 1 kV | 37/90 | 1.14 | 0 | 0.205 | 5.21 | 44 | 65 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×8 AWG 2 kV | 1 × 8 AWG (8.37 mm²) | 2 kV / 1 kV | 37/24 | 1.4 | 0 | 0.258 | 6.55 | 74 | 110 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×6 AWG 2 kV | 1 × 6 AWG (13.3 mm²) | 2 kV / 1 kV | 61/24 | 1.52 | 0 | 0.31 | 7.87 | 115 | 171 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×4 AWG 2 kV | 1 × 4 AWG (21.2 mm²) | 2 kV / 1 kV | 133/27 | 1.52 | 0 | 0.37 | 9.4 | 175 | 260 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×2 AWG 2 kV | 1 × 2 AWG (33.6 mm²) | 2 kV / 1 kV | 259/26 | 1.52 | 0 | 0.44 | 11.18 | 262 | 390 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×1 AWG 2 kV | 1 × 1 AWG (42.4 mm²) | 2 kV / 1 kV | 259/25 | 1.65 | 0 | 0.47 | 11.94 | 310 | 461 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×1/0 AWG 2 kV HD | 1 × 1/0 AWG (53.5 mm²) | 2 kV / 1 kV | 266/24 | 2.03 | 1.14 | 0.65 | 16.51 | 450 | 670 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×2/0 AWG 2 kV HD | 1 × 2/0 AWG (67.4 mm²) | 2 kV / 1 kV | 342/24 | 2.03 | 1.14 | 0.7 | 17.78 | 535 | 796 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×3/0 AWG 2 kV HD | 1 × 3/0 AWG (85.0 mm²) | 2 kV / 1 kV | 418/24 | 2.03 | 1.14 | 0.75 | 19.05 | 660 | 982 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×4/0 AWG 2 kV HD | 1 × 4/0 AWG (107 mm²) | 2 kV / 1 kV | 532/24 | 2.03 | 1.14 | 0.82 | 20.83 | 810 | 1205 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×262 kcmil 2 kV HD | 1 × 262 kcmil (133 mm²) | 2 kV / 1 kV | 646/24 | 2.29 | 1.65 | 0.92 | 23.37 | 985 | 1466 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×313 kcmil 2 kV HD | 1 × 313 kcmil (159 mm²) | 2 kV / 1 kV | 777/24 | 2.29 | 1.65 | 0.98 | 24.89 | 1170 | 1741 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×373 kcmil 2 kV HD | 1 × 373 kcmil (189 mm²) | 2 kV / 1 kV | 925/24 | 2.29 | 1.65 | 1.05 | 26.67 | 1345 | 2001 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×444 kcmil 2 kV HD | 1 × 444 kcmil (225 mm²) | 2 kV / 1 kV | 1110/24 | 2.29 | 1.65 | 1.12 | 28.45 | 1595 | 2373 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×535 kcmil 2 kV HD | 1 × 535 kcmil (271 mm²) | 2 kV / 1 kV | 1332/24 | 2.54 | 1.65 | 1.24 | 31.5 | 1955 | 2909 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×646 kcmil 2 kV HD | 1 × 646 kcmil (327 mm²) | 2 kV / 1 kV | 1591/24 | 2.54 | 1.65 | 1.33 | 33.78 | 2345 | 3490 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×777 kcmil 2 kV HD | 1 × 777 kcmil (394 mm²) | 2 kV / 1 kV | 1924/24 | 2.54 | 1.65 | 1.44 | 36.58 | 2755 | 4100 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×929 kcmil 2 kV HD | 1 × 929 kcmil (471 mm²) | 2 kV / 1 kV | 2300/24 | 2.54 | 1.65 | 1.54 | 39.12 | 3320 | 4940 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 1×1111 kcmil 2 kV HD | 1 × 1111 kcmil (563 mm²) | 2 kV / 1 kV | 2745/24 | 2.92 | 2.03 | 1.7 | 43.18 | 3925 | 5841 | Single-Core Power Unarmoured · 2 kV / 1 kV
| Type P 3C 14 AWG Unarmoured | 3 × 14 AWG (2.08 mm²) | 600 V / 2 kV | 19/27 | 1.14 | 1.52 | 0.45 | 11.4 | 118 | 176 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 12 AWG Unarmoured | 3 × 12 AWG (3.31 mm²) | 600 V / 2 kV | 19/25 | 1.14 | 1.52 | 0.49 | 12.4 | 148 | 220 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 10 AWG Unarmoured | 3 × 10 AWG (5.26 mm²) | 600 V / 2 kV | 37/24 | 1.14 | 1.52 | 0.56 | 14.2 | 205 | 305 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 8 AWG Unarmoured | 3 × 8 AWG (8.37 mm²) | 600 V / 2 kV | 37/24 | 1.52 | 1.65 | 0.72 | 18.3 | 320 | 476 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 6 AWG Unarmoured | 3 × 6 AWG (13.3 mm²) | 600 V / 2 kV | 61/24 | 1.52 | 2.03 | 0.84 | 21.3 | 450 | 670 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 4 AWG Unarmoured | 3 × 4 AWG (21.2 mm²) | 600 V / 2 kV | 133/27 | 1.52 | 2.03 | 0.98 | 24.9 | 650 | 967 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 2 AWG Unarmoured | 3 × 2 AWG (33.6 mm²) | 600 V / 2 kV | 259/26 | 1.52 | 2.03 | 1.14 | 29 | 940 | 1399 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 1/0 AWG Unarmoured | 3 × 1/0 AWG (53.5 mm²) | 600 V / 2 kV | 266/24 | 2.03 | 2.16 | 1.42 | 36.1 | 1460 | 2173 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 2/0 AWG Unarmoured | 3 × 2/0 AWG (67.4 mm²) | 600 V / 2 kV | 342/24 | 2.03 | 2.16 | 1.54 | 39.1 | 1780 | 2649 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 4/0 AWG Unarmoured | 3 × 4/0 AWG (107 mm²) | 600 V / 2 kV | 532/24 | 2.03 | 2.79 | 1.86 | 47.2 | 2680 | 3988 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 250 kcmil Unarmoured | 3 × 250 kcmil (127 mm²) | 600 V / 2 kV | 646/24 | 2.41 | 2.79 | 2.04 | 51.8 | 3190 | 4747 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 350 kcmil Unarmoured | 3 × 350 kcmil (177 mm²) | 600 V / 2 kV | 888/24 | 2.41 | 2.79 | 2.28 | 57.9 | 4250 | 6325 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 500 kcmil Unarmoured | 3 × 500 kcmil (253 mm²) | 600 V / 2 kV | 1221/24 | 2.41 | 3.18 | 2.62 | 66.5 | 5860 | 8721 | 3-Core Power Unarmoured · 600 V / 2 kV
| Type P 3C 14 AWG Armoured | 3 × 14 AWG (2.08 mm²) | 600 V / 2 kV | 19/27 | 1.14 | 1.52 | 0.57 | 14.5 | 210 | 313 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 12 AWG Armoured | 3 × 12 AWG (3.31 mm²) | 600 V / 2 kV | 19/25 | 1.14 | 1.52 | 0.61 | 15.5 | 250 | 372 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 10 AWG Armoured | 3 × 10 AWG (5.26 mm²) | 600 V / 2 kV | 37/24 | 1.14 | 1.52 | 0.68 | 17.3 | 325 | 484 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 8 AWG Armoured | 3 × 8 AWG (8.37 mm²) | 600 V / 2 kV | 37/24 | 1.52 | 2.03 | 0.86 | 21.8 | 480 | 714 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 6 AWG Armoured | 3 × 6 AWG (13.3 mm²) | 600 V / 2 kV | 61/24 | 1.52 | 2.03 | 0.98 | 24.9 | 640 | 952 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 4 AWG Armoured | 3 × 4 AWG (21.2 mm²) | 600 V / 2 kV | 133/27 | 1.52 | 2.03 | 1.14 | 29 | 890 | 1324 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 2 AWG Armoured | 3 × 2 AWG (33.6 mm²) | 600 V / 2 kV | 259/26 | 1.52 | 2.16 | 1.3 | 33 | 1240 | 1845 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 1/0 AWG Armoured | 3 × 1/0 AWG (53.5 mm²) | 600 V / 2 kV | 266/24 | 2.03 | 2.79 | 1.6 | 40.6 | 1850 | 2753 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 2/0 AWG Armoured | 3 × 2/0 AWG (67.4 mm²) | 600 V / 2 kV | 342/24 | 2.03 | 2.79 | 1.72 | 43.7 | 2210 | 3289 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 4/0 AWG Armoured | 3 × 4/0 AWG (107 mm²) | 600 V / 2 kV | 532/24 | 2.03 | 2.79 | 2.06 | 52.3 | 3240 | 4822 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 250 kcmil Armoured | 3 × 250 kcmil (127 mm²) | 600 V / 2 kV | 646/24 | 2.41 | 2.79 | 2.24 | 56.9 | 3820 | 5685 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 350 kcmil Armoured | 3 × 350 kcmil (177 mm²) | 600 V / 2 kV | 888/24 | 2.41 | 3.18 | 2.5 | 63.5 | 4980 | 7411 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P 3C 500 kcmil Armoured | 3 × 500 kcmil (253 mm²) | 600 V / 2 kV | 1221/24 | 2.41 | 3.56 | 2.86 | 72.6 | 6720 | 10000 | 3-Core Power Bronze-Braid Armoured · 600 V / 2 kV
| Type P VFD 3C 8 AWG Armoured | 3 × 8 AWG + 3 × 14 AWG Gnd | 2 kV / 1 kV | 37/24 | 1.4 | 2.03 | 0.849 | 21.56 | 529 | 787 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 6 AWG Armoured | 3 × 6 AWG + 3 × 12 AWG Gnd | 2 kV / 1 kV | 61/24 | 1.52 | 2.03 | 0.99 | 25.15 | 764 | 1137 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 4 AWG Armoured | 3 × 4 AWG + 3 × 12 AWG Gnd | 2 kV / 1 kV | 133/27 | 1.52 | 2.03 | 1.12 | 28.45 | 1020 | 1518 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 2 AWG Armoured | 3 × 2 AWG + 3 × 10 AWG Gnd | 2 kV / 1 kV | 259/26 | 1.52 | 2.03 | 1.271 | 32.28 | 1419 | 2112 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 1 AWG Armoured | 3 × 1 AWG + 3 × 10 AWG Gnd | 2 kV / 1 kV | 259/25 | 1.65 | 2.16 | 1.385 | 35.18 | 1692 | 2518 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 1/0 AWG Armoured | 3 × 1/0 AWG + 3 × 10 AWG Gnd | 2 kV / 1 kV | 266/24 | 2.03 | 2.16 | 1.49 | 37.85 | 1998 | 2973 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 2/0 AWG Armoured | 3 × 2/0 AWG + 3 × 10 AWG Gnd | 2 kV / 1 kV | 342/24 | 2.03 | 2.16 | 1.6 | 40.64 | 2407 | 3582 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 3/0 AWG Armoured | 3 × 3/0 AWG + 3 × 8 AWG Gnd | 2 kV / 1 kV | 418/24 | 2.03 | 2.79 | 1.797 | 45.64 | 2999 | 4463 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 4/0 AWG Armoured | 3 × 4/0 AWG + 3 × 8 AWG Gnd | 2 kV / 1 kV | 532/24 | 2.03 | 2.79 | 1.946 | 49.43 | 3622 | 5390 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 262 kcmil Armoured | 3 × 262 kcmil + 3 × 6 AWG Gnd | 2 kV / 1 kV | 646/24 | 2.29 | 2.79 | 2.176 | 55.27 | 4501 | 6698 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 313 kcmil Armoured | 3 × 313 kcmil + 3 × 6 AWG Gnd | 2 kV / 1 kV | 777/24 | 2.29 | 2.79 | 2.299 | 58.39 | 5152 | 7666 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 373 kcmil Armoured | 3 × 373 kcmil + 3 × 6 AWG Gnd | 2 kV / 1 kV | 925/24 | 2.29 | 2.79 | 2.449 | 62.2 | 5897 | 8775 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 444 kcmil Armoured | 3 × 444 kcmil + 3 × 6 AWG Gnd | 2 kV / 1 kV | 1110/24 | 2.29 | 2.79 | 2.6 | 66.04 | 6814 | 10140 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 535 kcmil Armoured | 3 × 535 kcmil + 3 × 4 AWG Gnd | 2 kV / 1 kV | 1332/24 | 2.54 | 3.56 | 2.862 | 72.69 | 8291 | 12337 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 646 kcmil Armoured | 3 × 646 kcmil + 3 × 4 AWG Gnd | 2 kV / 1 kV | 1591/24 | 2.54 | 3.56 | 3.063 | 77.8 | 9657 | 14370 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P VFD 3C 777 kcmil Armoured | 3 × 777 kcmil + 3 × 4 AWG Gnd | 2 kV / 1 kV | 1924/24 | 2.54 | 3.56 | 3.249 | 82.52 | 10767 | 16022 | 3-Core VFD Power Armoured & Sheathed · 2 kV / 1 kV
| Type P 1P 16 AWG OS Armoured | 1 Pair × 16 AWG (1.23 mm²) | 600 V (0.6/1 kV) | 19/29 | 0.76 | 1.5 | 0.54 | 13.7 | 200 | 300 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 2P 16 AWG IS/OS Armoured | 2 Pairs × 16 AWG (1.23 mm²) | 600 V (0.6/1 kV) | 19/29 | 0.76 | 1.5 | 0.77 | 19.6 | 360 | 535 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 4P 16 AWG IS/OS Armoured | 4 Pairs × 16 AWG (1.23 mm²) | 600 V (0.6/1 kV) | 19/29 | 0.76 | 2 | 0.9 | 22.9 | 520 | 775 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 8P 16 AWG IS/OS Armoured | 8 Pairs × 16 AWG (1.23 mm²) | 600 V (0.6/1 kV) | 19/29 | 0.76 | 2 | 1.14 | 29 | 855 | 1270 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 12P 16 AWG IS/OS Armoured | 12 Pairs × 16 AWG (1.23 mm²) | 600 V (0.6/1 kV) | 19/29 | 0.76 | 2 | 1.25 | 31.8 | 1030 | 1535 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 16P 16 AWG IS/OS Armoured | 16 Pairs × 16 AWG (1.23 mm²) | 600 V (0.6/1 kV) | 19/29 | 0.76 | 2 | 1.4 | 35.6 | 1275 | 1895 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 24P 16 AWG IS/OS Armoured | 24 Pairs × 16 AWG (1.23 mm²) | 600 V (0.6/1 kV) | 19/29 | 0.76 | 2.8 | 1.81 | 46 | 1730 | 2575 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 1P 14 AWG OS Armoured | 1 Pair × 14 AWG (1.94 mm²) | 600 V (0.6/1 kV) | 19/27 | 0.76 | 1.5 | 0.58 | 14.7 | 235 | 350 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 2P 14 AWG IS/OS Armoured | 2 Pairs × 14 AWG (1.94 mm²) | 600 V (0.6/1 kV) | 19/27 | 0.76 | 1.5 | 0.82 | 20.8 | 410 | 610 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 4P 14 AWG IS/OS Armoured | 4 Pairs × 14 AWG (1.94 mm²) | 600 V (0.6/1 kV) | 19/27 | 0.76 | 2 | 0.96 | 24.4 | 605 | 900 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 8P 14 AWG IS/OS Armoured | 8 Pairs × 14 AWG (1.94 mm²) | 600 V (0.6/1 kV) | 19/27 | 0.76 | 2 | 1.19 | 30.2 | 995 | 1480 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 12P 14 AWG IS/OS Armoured | 12 Pairs × 14 AWG (1.94 mm²) | 600 V (0.6/1 kV) | 19/27 | 0.76 | 2 | 1.38 | 35.1 | 1260 | 1875 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 16P 14 AWG IS/OS Armoured | 16 Pairs × 14 AWG (1.94 mm²) | 600 V (0.6/1 kV) | 19/27 | 0.76 | 2 | 1.52 | 38.6 | 1525 | 2270 | Shielded Multipair Signal Armoured & Sheathed · 600 V
| Type P 24P 14 AWG IS/OS Armoured | 24 Pairs × 14 AWG (1.94 mm²) | 600 V (0.6/1 kV) | 19/27 | 0.76 | 2.8 | 1.95 | 49.5 | 2440 | 3630 | Shielded Multipair Signal Armoured & Sheathed · 600 V
Single-conductor sizes 18 AWG through 1 AWG are single-extrusion XLPO (sheath thickness 0.00 mm); heavy-duty sizes 1/0 AWG through 1111 kcmil include a separate thermoset CPE outer jacket.
Armoured & sheathed constructions (PNBS) include an inner CPE bedding jacket, ≥ 88 % coverage braided bronze wire armour and an outer mud-resistant thermoset CPE sheath suitable for Class I Division 1 / Zone 1 hazardous locations.

## Technical data
IEEE 1580 Type P Marine & Offshore Drilling Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/ieee-1580-type-p-marine-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / UL 1309 Type X110 / CSA C22.2 No. 245. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage | 600 V / 2 kV (600 V (0.6/1 kV) & 2 kV/1000 V)
Key data | Conductor temp. | +110 / +125 °C (UL 1309 X110 · 125 °C XLPO compound)
Key data | Cold bend | −40 °C (−40 °C bend / −35 °C impact (CSA))
Key data | Armour option | Bronze braid (≥ 88 % coverage for Class I Div 1)
Key data | Min. bend radius | 6 × D / 8 × D (Unarmoured 6 × D · Armoured 8 × D)
Key data | Flame test | IEC 60332-3-22 (Cat. A & IEEE 1202 (70,000 BTU/hr))
Electrical | Rated voltage | 600 V (0.6/1 kV) & 2,000 V (2 kV/1000 V)
Electrical | Pair characteristic impedance | 68 Ω (16 & 14 AWG multipair); 60 Ω (1P 14 AWG)
Electrical | Pair mutual capacitance | 82 pF/m (25 pF/ft) nominal at 1 kHz
Electrical | Pair inductance | 0.39 mH/km (0.12 mH/kft) nominal
Thermal | Compound temperature rating | +125 °C continuous (Type P XLPO insulation)
Thermal | Shipboard certification rating | +110 °C (UL 1309 / CSA X110); +100 °C (IEEE 45)
Thermal | Short-circuit temperature | +250 °C (5 s maximum)
Thermal | Cold bend & cold impact | −40 °C cold bend / −35 °C cold impact (CSA 0.3)
Mechanical | Conductor construction | Soft annealed stranded tinned copper (ASTM B33)
Mechanical | Armour coverage | Braided bronze wire ≥ 88 % optical coverage
Mechanical | Minimum bend radius | 6 × D (unarmoured); 8 × D (armoured / VFD)
Resistance | Flame propagation | IEEE 1202 (70,000 BTU/hr) & IEC 60332-3-22 Cat. A
Resistance | Drilling mud & oil resistance | Ester-based drilling mud (Type P-MR), oil & fuel
Resistance | Hazardous location rating | Class I Div 1 / Zone 1 (armoured); Div 2 (unarmoured)
Standards | Primary design standards | IEEE 1580; IEEE 45; UL 1309; CSA C22.2 No. 245
Standards | Offshore & marine rules | API RP 14F; USCG 46 CFR; ABS; DNV; Lloyd's Register
Standards | Tray & exposed run | UL 1277 Type TC-ER; CSA C22.2 No. 239 Type CIC
Identification | Core identification | ICEA Method 1 or numbered cores; pairs black/white
Identification | Outer sheath colour | Black thermoset CPE or arctic neoprene (Type N)

## Construction
IEEE 1580 Type P Marine & Offshore Drilling Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/ieee-1580-type-p-marine-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / UL 1309 Type X110 / CSA C22.2 No. 245. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Flexible tinned copper conductor | Soft annealed stranded tinned copper per ASTM B33 (high strand count Class I/K for power; 19-strand for control/signal) with polyester separator tape | ASTM B33 / IEEE 1580
2 | Type P cross-linked polyolefin (XLPO) insulation | Chemically or electron-beam cross-linked flame-retardant polyolefin (Type P), 125 °C compound rating (UL 1309 Type X110) | IEEE 1580 Table 25 / UL 1309
3 | Foil/braid EMI screen (VFD & signal constructions) | 100 % coverage aluminium/polyester tape with tinned copper drain wire (multipair/signal) or dual copper tape / combination shield (VFD) | IEEE 1580
4 | Inner thermoset CPE bedding jacket | Flame-retardant thermosetting chlorinated polyethylene (CPE) or arctic neoprene (Type N) inner jacket per IEEE 1580 | IEEE 1580
5 | Braided bronze wire armour (armoured & sheathed types) | Corrosion-resistant braided bronze wire with minimum 88 % optical coverage for mechanical crush protection and Class I Div 1 rating | IEEE 1580 / IEEE 45
6 | Mud-resistant thermoset CPE outer sheath | Heavy-duty thermosetting chlorinated polyethylene (CPE, Type P-MR) resistant to ester/calcium-bromide drilling muds, oil, UV and salt spray | IEEE 1580 / UL 1309
| Type P Unarmoured (P / PN) | Single-core or multi-core XLPO-insulated cable with a heavy-duty thermoset CPE outer jacket for Class I Division 2 / Zone 2 cable trays and Type TC-ER exposed runs.
| Type P Armoured & Sheathed (PNBS) | Includes inner CPE bedding, ≥ 88 % braided bronze wire armour and outer mud-resistant CPE sheath for Class I Division 1 / Zone 1 hazardous areas.
| Type P VFD Symmetrical Ground (VFD-PNBS) | Three phase conductors with three symmetrical split earth conductors, overall EMC shielding, bronze braid armour and CPE outer sheath for 2 kV AC drilling drives.

## Series
IEEE 1580 Type P Marine & Offshore Drilling Cable – Series
TEBAOFLEX ¦ https://tebaoflex.com/cables/ieee-1580-type-p-marine-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / UL 1309 Type X110 / CSA C22.2 No. 245. Values for your order are confirmed in the quotation.
Code | Series | Rating | Standard / class | Sizes | Typical use
Type P 1C Power | Single-Conductor Unarmoured Power | 600 V & 2 kV/1000 V | IEEE 1580 / UL 1309 X110 | 23 | DC/AC traction bus, mud pump feeders & top-drive power loops
Type P 3C Unarmoured | Three-Conductor Unarmoured Power | 600 V / 2 kV | IEEE 1580 / UL 1277 TC-ER | 13 | Three-phase motors, deck machinery & Zone 2 distribution
Type P 3C Armoured | Three-Conductor Bronze-Braid Armoured | 600 V / 2 kV | IEEE 1580 / Class I Div 1 | 13 | Class I Division 1 / Zone 1 drilling modules & shipboard power
Type P VFD Power | Symmetrical-Ground VFD Armoured & Sheathed | 2 kV / 1000 V | IEEE 1580 / 2 kV VFD | 16 | 2 kV PWM inverter drives for drawworks, mud pumps & thrusters
Type P Multipair Signal | Individual & Overall Shielded Multipair (IS/OS) | 600 V (0.6/1 kV) | IEEE 1580 / UL 1309 | 14 | 4–20 mA process loops, PLC I/O, fire & gas and rig instrumentation

## Quality and supply
IEEE 1580 Type P Marine & Offshore Drilling Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/ieee-1580-type-p-marine-offshore-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEEE 1580 / UL 1309 Type X110 / CSA C22.2 No. 245. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor DC resistance & high-voltage AC dielectric test — 100 % reel verification of tinned copper DC resistance (ASTM B33) and AC dielectric withstand per IEEE 1580 / UL 1309 | Every production length
Type test | Vertical tray flame propagation (IEEE 1202 & IEC 60332-3-22 Cat. A) — Char height ≤ 1.5 m under 70,000 BTU/hr burner per IEEE 1202 / CSA FT4 and IEC 60332-3-22 Category A | Type approval & periodic audit
Type test | Ester-based drilling mud, oil & fuel immersion (Type P-MR) — Retention of tensile strength and elongation after hot oil and ester-based drilling fluid immersion per IEEE 1580 | Type approval
Type test | Arctic cold bend (−40 °C) and cold impact (−35 °C) — No sheath or insulation cracking under −40 °C mandrel bend and −35 °C impact test per CSA C22.2 No. 0.3 / UL 1309 | Type approval & periodic sample
Standard / approval | IEEE Std 1580 & IEEE Std 45 Marine Shipboard Cable
Standard / approval | UL 1309 & CSA C22.2 No. 245 Listed Type X110 (110 °C)
Standard / approval | USCG 46 CFR, ABS, DNV & Lloyd's Register Type Approval
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX — IEEE 1580 TYPE P-MR — <SIZE> — XLPO/CPE — 600V OR 2000V — UL 1309 / CSA 245 TYPE X110 110C — IEC 60332-3-22 CAT A — IEEE 1202 FT4 -40C
Supply | Standard packing: 1,000 ft (305 m) or 2,000 ft (610 m) export seaworthy wooden drums
Supply | Armour options: Unarmoured (Zone 2 / Div 2) or braided bronze armour + outer CPE sheath (Zone 1 / Div 1)
Supply | Jacket compounds: Thermoset CPE (standard mud-resistant) or arctic neoprene (Type N)
Supply | Export tariff code: HS 8544.49 (≤ 1,000 V) / HS 8544.60 (> 1,000 V)