## Request a quote
Request a quotation for J-H(st)H
Application engineer · LSZH building & fire-alarm cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/j-h-st-h-halogen-free-installation-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
J-H(st)H Halogen-Free Installation Cable – Dimensions & weights (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-h-st-h-halogen-free-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-H(St)H...Bd) · LSZH. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| J-H(St)H 1×2×0.6 Bd | 1×2×0.6 | 23 (0.6 mm) | 4.3 | 4.7 | 6 | 28 | 38 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 2×2×0.6 Bd | 2×2×0.6 | 23 (0.6 mm) | 5 | 5.4 | 12 | 38 | 43 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 4×2×0.6 Bd | 4×2×0.6 | 23 (0.6 mm) | 6.2 | 6.7 | 23 | 62 | 54 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 6×2×0.6 Bd | 6×2×0.6 | 23 (0.6 mm) | 6.9 | 7.5 | 34 | 81 | 60 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 10×2×0.6 Bd | 10×2×0.6 | 23 (0.6 mm) | 8.4 | 9.1 | 56 | 122 | 73 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 20×2×0.6 Bd | 20×2×0.6 | 23 (0.6 mm) | 10.9 | 11.8 | 112 | 220 | 94 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 30×2×0.6 Bd | 30×2×0.6 | 23 (0.6 mm) | 13 | 14.1 | 168 | 315 | 113 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 40×2×0.6 Bd | 40×2×0.6 | 23 (0.6 mm) | 14.7 | 16 | 223 | 410 | 128 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 1×2×0.8 Bd | 1×2×0.8 | 20 | 5.1 | 5.5 | 11 | 39 | 44 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 2×2×0.8 Bd | 2×2×0.8 | 20 | 5.7 | 6.2 | 21 | 56 | 50 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 4×2×0.8 Bd | 4×2×0.8 | 20 | 7.8 | 8.5 | 41 | 98 | 68 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 6×2×0.8 Bd | 6×2×0.8 | 20 | 9 | 9.8 | 61 | 136 | 78 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 10×2×0.8 Bd | 10×2×0.8 | 20 | 11.1 | 12.1 | 101 | 210 | 97 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 12×2×0.8 Bd | 12×2×0.8 | 20 | 12 | 13 | 121 | 246 | 104 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) LSZH DIN VDE 0815
| J-H(St)H 20×2×0.8 Bd | 20×2×0.8 | 20 | 14.9 | 16.2 | 201 | 395 | 130 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) LSZH DIN VDE 0815
Dimensions and weights are typical values per DIN VDE 0815 (J-H(St)H...Bd) · LSZH. Minimum fixed bending radius shown is 8 × OD.

## Electrical & current ratings
J-H(st)H Halogen-Free Installation Cable – Electrical & current ratings (2)
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-h-st-h-halogen-free-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-H(St)H...Bd) · LSZH. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single pair/core 30 °C, A | Multi-core bundle 30 °C, A
0.28 | 23 (0.6 mm) | 65 | 4.0 | 3.0
0.5 | 20 | 39 | 9.0 | 6.0
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / DIN VDE 0891-1. Apply grouping derating factors for multi-core control and signal bundles.

## Technical data
J-H(st)H Halogen-Free Installation Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-h-st-h-halogen-free-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-H(St)H...Bd) · LSZH. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Peak voltage | 300 V (Peak operating voltage (not for power))
Key data | Halogen-free | IEC 60754-1/2 (Zero halogen · pH ≥ 4.3 · ≤ 10 µS/mm)
Key data | Smoke density | IEC 61034-2 (≥ 60 % light transmittance in fire)
Key data | Conductors | Ø 0.6 / 0.8 mm (Solid Cu (≈0.28/0.50 mm²) in pairs)
Key data | Static screen | Al/PET (St) (Plastic-laminated Al foil + drain wire)
Key data | Pair range | 1×2 to 40×2 (Unit bundles (Bd) · Grey or Red sheath)
Electrical | Peak operating voltage | 300 V (not permitted for heavy current power installation)
Electrical | AC test voltage (50 Hz) | 800 V AC (core/core & core/screen)
Electrical | Max. loop resistance (20 °C) | Ø 0.6 mm: ≤ 130 Ω/km · Ø 0.8 mm: ≤ 73.2 Ω/km
Electrical | Mutual capacitance (800 Hz) | ≤ 120 nF/km
Electrical | Capacitive coupling (k₁) | ≤ 300 pF / 100 m at 800 Hz
Electrical | Insulation resistance | ≥ 100 MΩ·km at +20 °C
Thermal | Temperature, during installation | −5 °C to +50 °C
Thermal | Temperature, fixed operation | −30 °C to +70 °C
Mechanical | Min. bending radius, fixed | 7.5 × overall diameter (single bend during installation: 2.5 × OD)
Mechanical | Stranding method (Bd) | 2 cores twisted into a pair (2×2 as star-quad); 4 pairs stranded into unit bundles ('Bündelverseilung')
Mechanical | Conductor type | Solid annealed copper wire (Ø 0.6 mm or Ø 0.8 mm) for IDC / LSA-Plus blocks
Resistance | Halogen-free & non-corrosive | IEC 60754-1 / EN 60754-1 & IEC 60754-2 (pH ≥ 4.3, conductivity ≤ 10 µS/mm)
Resistance | Low smoke emission | IEC 61034-2 / EN 61034-2 (≥ 60 % light transmittance)
Resistance | Flame retardance | IEC 60332-1-2 & IEC 60332-3-24 Cat. C bunched vertical flame test
Standards | Primary standard | DIN VDE 0815 (J-H(St)H...Bd)
Standards | Fire safety standards | IEC 60754-1/2, IEC 61034-2, IEC 60332-1-2 / 60332-3-24
Standards | PVC counterpart | See J-Y(St)Y...Lg for standard PVC indoor installations
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Pebble-grey (RAL 7032) or flame-red (RAL 3000 for Brandmeldekabel)
Identification | Pair identification | DIN VDE 0815 pair & ring colour sequence (Pair 1 red/black, Pair 2 white/yellow…)
Identification | Sheath marking | TEBAOFLEX J-H(St)H [n×2×0.6/0.8] Bd HALOGEN-FREE DIN VDE 0815 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
J-H(st)H Halogen-Free Installation Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-h-st-h-halogen-free-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-H(St)H...Bd) · LSZH. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper conductor | Solid circular annealed copper wire Ø 0.6 mm (≈ 0.28 mm²) or Ø 0.8 mm (≈ 0.50 mm²) for LSA/IDC termination | DIN VDE 0815 / IEC 60228 Cl. 1
2 | Halogen-free LSZH core insulation (H) | Cross-linked or thermoplastic halogen-free polyolefin compound Type HI1 / HI2 (DIN VDE 0207-24) | DIN VDE 0815 · HI2
3 | Halogen-free wrapping tape | Overlapped halogen-free plastic tape over the paired unit bundles ('Bd') | DIN VDE 0815
4 | Static Al/PET foil screen (St) | Plastic-laminated aluminium foil tape with a longitudinal solid tinned-copper drain wire | DIN VDE 0815
5 | Halogen-free LSZH outer sheath (H) | Flame-retardant low-smoke zero-halogen compound Type HM2, pebble-grey RAL 7032 (or red RAL 3000 for fire alarm) | DIN VDE 0207-24 HM2 · IEC 60332-3-24
| J-H(St)H...Bd Ø 0.6 mm Grey RAL 7032 | Halogen-free telecommunications, intercom and LSA punch-down installation cable from 1×2×0.6 to 40×2×0.6
| J-H(St)H...Bd Ø 0.8 mm Grey RAL 7032 | Halogen-free BMS, HVAC actuator and sensor bus cable from 1×2×0.8 to 20×2×0.8 (loop ≤ 73.2 Ω/km)
| J-H(St)H...Bd Ø 0.8 mm Red RAL 3000 (Brandmeldekabel) | Halogen-free red fire-alarm loop cable ('Brandmeldekabel') for public buildings

## Quality and supply
J-H(st)H Halogen-Free Installation Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-h-st-h-halogen-free-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-H(St)H...Bd) · LSZH. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 0.8 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / DIN VDE 0815 (J-H(St)H...Bd) · LSZH (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath material physical properties — DIN VDE 0815 (J-H(St)H...Bd) · LSZH | Type approval
Standard / approval | DIN VDE 0815 (J-H(St)H...Bd) · LSZH
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX J-H(St)H [n×2×0.6/0.8] Bd HALOGEN-FREE DIN VDE 0815 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pair counts or sheath colours on request