## Request a quote
Request a quotation for J-Y(st)Y
Application engineer · building automation & telecom cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/j-y-st-y-screened-installation-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
J-Y(st)Y Screened Installation Cable – Dimensions & weights (15)
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-y-st-y-screened-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-Y(St)Y...Lg). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| J-Y(St)Y 1×2×0.6 Lg | 1×2×0.6 | 23 (0.6 mm) | 4.1 | 4.5 | 6 | 26 | 36 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) DIN VDE 0815
| J-Y(St)Y 2×2×0.6 Lg | 2×2×0.6 | 23 (0.6 mm) | 4.8 | 5.2 | 12 | 35 | 42 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) DIN VDE 0815
| J-Y(St)Y 4×2×0.6 Lg | 4×2×0.6 | 23 (0.6 mm) | 6 | 6.5 | 23 | 58 | 52 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) DIN VDE 0815
| J-Y(St)Y 6×2×0.6 Lg | 6×2×0.6 | 23 (0.6 mm) | 6.7 | 7.3 | 34 | 76 | 58 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) DIN VDE 0815
| J-Y(St)Y 10×2×0.6 Lg | 10×2×0.6 | 23 (0.6 mm) | 8.1 | 8.8 | 56 | 114 | 70 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) DIN VDE 0815
| J-Y(St)Y 20×2×0.6 Lg | 20×2×0.6 | 23 (0.6 mm) | 10.6 | 11.5 | 112 | 208 | 92 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) DIN VDE 0815
| J-Y(St)Y 30×2×0.6 Lg | 30×2×0.6 | 23 (0.6 mm) | 12.7 | 13.8 | 168 | 298 | 110 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) DIN VDE 0815
| J-Y(St)Y 40×2×0.6 Lg | 40×2×0.6 | 23 (0.6 mm) | 14.4 | 15.6 | 223 | 388 | 125 | n × 2 × 0.6 mm (Ø Solid Cu, Loop ≤ 130 Ω/km) DIN VDE 0815
| J-Y(St)Y 1×2×0.8 Lg | 1×2×0.8 | 20 | 4.9 | 5.3 | 11 | 36 | 42 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) DIN VDE 0815
| J-Y(St)Y 2×2×0.8 Lg | 2×2×0.8 | 20 | 5.5 | 6 | 21 | 52 | 48 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) DIN VDE 0815
| J-Y(St)Y 4×2×0.8 Lg | 4×2×0.8 | 20 | 7.5 | 8.2 | 41 | 92 | 66 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) DIN VDE 0815
| J-Y(St)Y 6×2×0.8 Lg | 6×2×0.8 | 20 | 8.7 | 9.5 | 61 | 128 | 76 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) DIN VDE 0815
| J-Y(St)Y 10×2×0.8 Lg | 10×2×0.8 | 20 | 10.9 | 11.8 | 101 | 198 | 94 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) DIN VDE 0815
| J-Y(St)Y 12×2×0.8 Lg | 12×2×0.8 | 20 | 11.6 | 12.6 | 121 | 232 | 101 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) DIN VDE 0815
| J-Y(St)Y 20×2×0.8 Lg | 20×2×0.8 | 20 | 14.5 | 15.8 | 201 | 372 | 126 | n × 2 × 0.8 mm (Ø Solid Cu, Loop ≤ 73.2 Ω/km) DIN VDE 0815
Dimensions and weights are typical values per DIN VDE 0815 (J-Y(St)Y...Lg). Minimum fixed bending radius shown is 8 × OD.

## Electrical & current ratings
J-Y(st)Y Screened Installation Cable – Electrical & current ratings (2)
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-y-st-y-screened-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-Y(St)Y...Lg). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single pair/core 30 °C, A | Multi-core bundle 30 °C, A
0.28 | 23 (0.6 mm) | 65 | 4.0 | 3.0
0.5 | 20 | 39 | 9.0 | 6.0
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / DIN VDE 0891-1. Apply grouping derating factors for multi-core control and signal bundles.

## Technical data
J-Y(st)Y Screened Installation Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-y-st-y-screened-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-Y(St)Y...Lg). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Peak voltage | 300 V (Peak operating voltage (not for power))
Key data | Test voltage | 800 V AC (50 Hz core/core & core/screen)
Key data | Conductors | Ø 0.6 / 0.8 mm (Solid Cu (≈0.28/0.50 mm²) in pairs)
Key data | Static screen | Al/PET (St) (Plastic-laminated Al foil + drain wire)
Key data | Capacitance | ≤ 100 nF/km (Max. mutual capacitance at 800 Hz)
Key data | Pair range | 1×2 to 40×2 (Layered pairs (Lg) · Grey or Red sheath)
Electrical | Peak operating voltage | 300 V (not permitted for heavy current power installation)
Electrical | AC test voltage (50 Hz) | 800 V AC (core/core & core/screen)
Electrical | Max. loop resistance (20 °C) | Ø 0.6 mm: ≤ 130 Ω/km · Ø 0.8 mm: ≤ 73.2 Ω/km
Electrical | Mutual capacitance (800 Hz) | ≤ 100 nF/km (up to 4 pairs may exceed by 20 %)
Electrical | Capacitive coupling (k₁) | ≤ 300 pF / 100 m at 800 Hz
Electrical | Insulation resistance | ≥ 100 MΩ·km at +20 °C
Thermal | Temperature, during installation | −5 °C to +50 °C
Thermal | Temperature, fixed operation | −30 °C to +70 °C
Mechanical | Min. bending radius, fixed | 7.5 × overall diameter (single bend during installation: 2.5 × OD)
Mechanical | Stranding method (Lg) | 2 cores twisted into a pair; pairs stranded in concentric layers ('Lagenverseilung')
Mechanical | Conductor type | Solid annealed copper wire (Ø 0.6 mm or Ø 0.8 mm) for IDC / LSA-Plus blocks
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2 self-extinguishing · CPR Eca
Resistance | Installation environment | For dry and damp rooms on, in and under plaster, as well as fixed outdoor walls protected from direct sun
Standards | Primary standard | DIN VDE 0815 (J-Y(St)Y...Lg)
Standards | Pair colour code (Lg) | Pair 1: red/black · Pair 2: white/yellow · Pair 3: white/green · Pair 4: white/brown · Pair 5: white/blue (repeated per layer)
Standards | Halogen-free counterpart | See J-H(St)H...Bd / Lg for low-smoke zero-halogen buildings
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Pebble-grey (RAL 7032), flame-red (RAL 3000 for fire alarm), or green (RAL 6018 for EIB/KNX)
Identification | Pair identification | DIN VDE 0815 concentric layer pair colour sequence (Pair 1 red/black)
Identification | Sheath marking | TEBAOFLEX J-Y(St)Y [n×2×0.6/0.8] Lg DIN VDE 0815 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
J-Y(st)Y Screened Installation Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-y-st-y-screened-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-Y(St)Y...Lg). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper conductor | Solid circular annealed copper wire Ø 0.6 mm (≈ 0.28 mm²) or Ø 0.8 mm (≈ 0.50 mm²) for gas-tight LSA/IDC termination | DIN VDE 0815 / IEC 60228 Cl. 1
2 | PVC core insulation (Y) | Thermoplastic PVC compound Type YI1 (DIN VDE 0207-4) twisted in pairs and laid up in layers ('Lg') | DIN VDE 0815 · YI1
3 | Plastic wrapping foil | Overlapped polyester separator tape over the layered pair assembly | DIN VDE 0815
4 | Static Al/PET foil screen (St) | Plastic-laminated aluminium foil tape with a longitudinal solid tinned-copper drain wire | DIN VDE 0815
5 | PVC outer sheath (Y) | Flame-retardant polyvinyl chloride compound Type YM1, pebble-grey RAL 7032 (or flame-red RAL 3000 for fire alarm) | DIN VDE 0207-5 YM1 · IEC 60332-1-2
| J-Y(St)Y...Lg Ø 0.6 mm Grey RAL 7032 | Standard telecommunications, intercom and LSA punch-down installation cable from 1×2×0.6 to 40×2×0.6
| J-Y(St)Y...Lg Ø 0.8 mm Grey RAL 7032 | Low-loop-resistance (≤ 73.2 Ω/km) BMS, HVAC actuator and long-run sensor cable from 1×2×0.8 to 20×2×0.8
| J-Y(St)Y...Lg Ø 0.8 mm Red RAL 3000 (Brandmeldekabel) | Red outer sheath printed 'Brandmeldekabel' for fire detection and alarm loop identification

## Quality and supply
J-Y(st)Y Screened Installation Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/j-y-st-y-screened-installation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (J-Y(St)Y...Lg). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 0.8 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / DIN VDE 0815 (J-Y(St)Y...Lg) (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath material physical properties — DIN VDE 0815 (J-Y(St)Y...Lg) | Type approval
Standard / approval | DIN VDE 0815 (J-Y(St)Y...Lg)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX J-Y(St)Y [n×2×0.6/0.8] Lg DIN VDE 0815 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pair counts or sheath colours on request