## Request a quote
Request a quotation for JE-LiYCY
Application engineer · process plant & DCS marshalling cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/je-liycy-screened-industrial-electronic-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
JE-LiYCY Screened Industrial Electronic Cable – Dimensions & weights (8)
TEBAOFLEX ¦ https://tebaoflex.com/cables/je-liycy-screened-industrial-electronic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (JE-LiYCY...Bd). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| JE-LiYCY 2×2×0.5 Bd | 2×2×0.5 | 20 | 5.7 | 6.2 | 35 | 58 | 37 | n × 2 × 0.5 mm² (7×0.30 mm) Paired Unit-Bundle Configurations (DIN VDE 0815)
| JE-LiYCY 4×2×0.5 Bd | 4×2×0.5 | 20 | 7.8 | 8.5 | 62 | 102 | 51 | n × 2 × 0.5 mm² (7×0.30 mm) Paired Unit-Bundle Configurations (DIN VDE 0815)
| JE-LiYCY 8×2×0.5 Bd | 8×2×0.5 | 20 | 10.9 | 11.8 | 116 | 192 | 71 | n × 2 × 0.5 mm² (7×0.30 mm) Paired Unit-Bundle Configurations (DIN VDE 0815)
| JE-LiYCY 12×2×0.5 Bd | 12×2×0.5 | 20 | 12.5 | 13.6 | 168 | 272 | 82 | n × 2 × 0.5 mm² (7×0.30 mm) Paired Unit-Bundle Configurations (DIN VDE 0815)
| JE-LiYCY 16×2×0.5 Bd | 16×2×0.5 | 20 | 13.9 | 15.1 | 218 | 348 | 91 | n × 2 × 0.5 mm² (7×0.30 mm) Paired Unit-Bundle Configurations (DIN VDE 0815)
| JE-LiYCY 20×2×0.5 Bd | 20×2×0.5 | 20 | 15.5 | 16.9 | 268 | 428 | 101 | n × 2 × 0.5 mm² (7×0.30 mm) Paired Unit-Bundle Configurations (DIN VDE 0815)
| JE-LiYCY 24×2×0.5 Bd | 24×2×0.5 | 20 | 17.1 | 18.6 | 320 | 508 | 112 | n × 2 × 0.5 mm² (7×0.30 mm) Paired Unit-Bundle Configurations (DIN VDE 0815)
| JE-LiYCY 32×2×0.5 Bd | 32×2×0.5 | 20 | 19.1 | 20.8 | 422 | 668 | 125 | n × 2 × 0.5 mm² (7×0.30 mm) Paired Unit-Bundle Configurations (DIN VDE 0815)
Dimensions and weights are typical values per DIN VDE 0815 (JE-LiYCY...Bd). Minimum fixed bending radius shown is 6 × OD.

## Electrical & current ratings
JE-LiYCY Screened Industrial Electronic Cable – Electrical & current ratings (1)
TEBAOFLEX ¦ https://tebaoflex.com/cables/je-liycy-screened-industrial-electronic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (JE-LiYCY...Bd). Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single pair/core 30 °C, A | Multi-core bundle 30 °C, A
0.5 | 20 | 39 | 9.0 | 6.0
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / DIN VDE 0891-1. Apply grouping derating factors for multi-core control and signal bundles.

## Technical data
JE-LiYCY Screened Industrial Electronic Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/je-liycy-screened-industrial-electronic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (JE-LiYCY...Bd). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Peak voltage | 225 V (Peak operating voltage (DIN VDE 0815))
Key data | Test voltage | 500 / 2000 V (500 V core/core · 2000 V core/screen)
Key data | Conductor | 0.5 mm² (7×0.3) (7-wire stranded Cu · loop ≤ 78.4 Ω/km)
Key data | Stranding | 4-pair bundles (Twisted pairs in unit bundles (Bd))
Key data | EMC screen | ≥ 80 % CuSn (Overall tinned-copper wire braid (C))
Key data | Pair range | 2×2 to 32×2 (Grey RAL 7032 or Blue RAL 5015 (Ex-i))
Electrical | Peak operating voltage | 225 V (not permitted for heavy current power installation)
Electrical | AC test voltage (50 Hz) | 500 V AC (core/core) · 2000 V AC (core/screen)
Electrical | Max. loop resistance (20 °C) | ≤ 78.4 Ω/km (single conductor ≤ 39.2 Ω/km)
Electrical | Mutual capacitance (800 Hz) | ≤ 100 nF/km (core/core) — up to 4 pairs may exceed by 20 %
Electrical | Inductance & L/R ratio | Approx. 0.65 mH/km (suited for EN 60079-14 Ex-i circuits)
Electrical | Insulation resistance | ≥ 100 MΩ·km at +20 °C
Thermal | Temperature, flexing / installation | −5 °C to +50 °C
Thermal | Temperature, fixed operation | −30 °C to +70 °C
Mechanical | Min. bending radius, fixed | 6 × overall diameter
Mechanical | Min. bending radius, flexing | 15 × overall diameter
Mechanical | Conductor stranding | 7 × 0.30 mm (0.5 mm²) stranded bare copper ('Li')
Mechanical | Unit bundle stranding (Bd) | 4 twisted pairs per bundle (2×2×0.5 stranded as star-quad)
Resistance | Flame retardance | IEC 60332-1-2 / EN 60332-1-2 self-extinguishing · CPR Eca
Resistance | EMC & Ex-i safety | 2000 V core-to-screen dielectric strength + ≥ 80 % tinned-Cu braid screen
Standards | Primary standard | DIN VDE 0815 (JE-LiYCY...Bd)
Standards | Pair colour code within bundle | Pair 1: blue/red · Pair 2: grey/yellow · Pair 3: green/brown · Pair 4: white/black (with bundle ring code)
Standards | Ex-i installation | EN 60079-14 / VDE 0165-1 (RAL 5015 blue sheath version)
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Pebble-grey (RAL 7032) or sky-blue (RAL 5015 for Ex-i 'EB')
Identification | Bundle & pair identification | DIN VDE 0815 4-pair bundle colour code + ring group marks
Identification | Sheath marking | TEBAOFLEX JE-LiYCY [n×2×0.5] Bd DIN VDE 0815 CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
JE-LiYCY Screened Industrial Electronic Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/je-liycy-screened-industrial-electronic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (JE-LiYCY...Bd). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | 7-wire stranded copper conductor | Annealed bare copper 0.5 mm² (7 × 0.30 mm, Class 2) combining vibration resistance with firm terminal clamping | DIN VDE 0815
2 | PVC core insulation (Y) | Semi-rigid PVC compound Type YI2 (DIN VDE 0207-4) with DIN VDE 0815 pair & bundle ring markings | DIN VDE 0815 · YI2
3 | Paired 4-pair unit bundles (Bd) | 2 cores twisted into a pair; 4 pairs stranded into a numbered unit bundle ('Bündelverseilung') | DIN VDE 0815
4 | PET tape + tinned-copper braid (C) | Overlapped polyester tape plus ≥ 80 % optical coverage tinned-copper wire braid tested at 2000 V AC core/screen | DIN VDE 0815 · EN 60079-14
5 | PVC outer sheath (Y) | Flame-retardant polyvinyl chloride compound Type YM1, pebble-grey RAL 7032 or sky-blue RAL 5015 (Ex-i) | DIN VDE 0207-5 YM1 · IEC 60332-1-2
| JE-LiYCY...Bd Grey RAL 7032 (2×2×0.5 to 32×2×0.5) | Standard industrial process control and DCS/PLC marshalling cable with 4-pair unit bundles
| JE-LiYCY...Bd EB Sky-Blue RAL 5015 (Ex-i Intrinsically Safe) | Sky-blue outer sheath ('Eigensicher') meeting EN 60079-14 inductance/capacitance ratio limits for Zone 1/2 Ex-i loops

## Quality and supply
JE-LiYCY Screened Industrial Electronic Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/je-liycy-screened-industrial-electronic-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0815 (JE-LiYCY...Bd). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / DIN VDE 0815 (JE-LiYCY...Bd) (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath material physical properties — DIN VDE 0815 (JE-LiYCY...Bd) | Type approval
Standard / approval | DIN VDE 0815 (JE-LiYCY...Bd)
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX JE-LiYCY [n×2×0.5] Bd DIN VDE 0815 CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pair counts or sheath colours on request