## Request a quote
Request a quotation for JX / Type J extension
Application engineer · temperature & process instrumentation
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/jx-thermocouple-extension-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
JX / Type J extension Thermocouple Cable – Dimensions, construction & weights (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/jx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Insulation / Sheath | Temp. range | Outer Ø ≈ mm | Weight ≈ kg/km | Min. bend R fixed mm | Series
| JX-PVC-OS 1×2×0.5 | 1×2×0.5 mm² (7/0.30) | PVC / PVC (OS) | −25…+105 °C | 5.6 | 43 | 42 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-PiMF 2×2×0.5 | 2×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+105 °C | 8.6 | 82 | 64 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-PiMF 4×2×0.5 | 4×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+105 °C | 10.8 | 139 | 81 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-PiMF 8×2×0.5 | 8×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+105 °C | 14.1 | 242 | 106 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-PiMF 12×2×0.5 | 12×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+105 °C | 16.9 | 342 | 127 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-OS 1×2×1.0 | 1×2×1.0 mm² (7/0.43) | PVC / PVC (OS) | −25…+105 °C | 6.7 | 66 | 50 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-PiMF 4×2×1.0 | 4×2×1.0 mm² (7/0.43) | PVC / PVC (PiMF+OS) | −25…+105 °C | 12.8 | 208 | 96 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-OS 1×2×1.5 | 1×2×1.5 mm² (7/0.53) | PVC / PVC (OS) | −25…+105 °C | 7.5 | 90 | 56 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-PiMF 4×2×1.5 | 4×2×1.5 mm² (7/0.53) | PVC / PVC (PiMF+OS) | −25…+105 °C | 14.3 | 280 | 107 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-PVC-PiMF 12×2×1.5 | 12×2×1.5 mm² (7/0.53) | PVC / PVC (PiMF+OS) | −25…+105 °C | 22.6 | 698 | 170 | JX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| JX-FEP-OS 1×2×0.5 | 1×2×0.5 mm² (7/0.30) | FEP / FEP (OS) | −60…+200 °C | 4.6 | 37 | 34 | JX High-Temperature FEP / FEP Screened (−60…+200 °C)
| JX-FEP-PiMF 4×2×0.5 | 4×2×0.5 mm² (7/0.30) | FEP / FEP (PiMF+OS) | −60…+200 °C | 9.2 | 125 | 69 | JX High-Temperature FEP / FEP Screened (−60…+200 °C)
| JX-FEP-OS 1×2×1.0 | 1×2×1.0 mm² (7/0.43) | FEP / FEP (OS) | −60…+200 °C | 5.6 | 57 | 42 | JX High-Temperature FEP / FEP Screened (−60…+200 °C)
| JX-XLPE-SWA 1×2×1.5 | 1×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | −40…+90 °C | 12.1 | 294 | 121 | JX XLPE / LSZH / SWA Armoured Direct-Burial (−40…+90 °C)
| JX-XLPE-SWA 4×2×1.5 | 4×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | −40…+90 °C | 19.8 | 738 | 198 | JX XLPE / LSZH / SWA Armoured Direct-Burial (−40…+90 °C)
| JX-XLPE-SWA 8×2×1.5 | 8×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | −40…+90 °C | 25 | 1168 | 250 | JX XLPE / LSZH / SWA Armoured Direct-Burial (−40…+90 °C)
Specify 'IEC' (+ Black / − White) or 'ANSI' (+ White / − Red) colour coding when ordering.

## Loop resistance & EMF parameter
JX / Type J extension Thermocouple Cable – Loop resistance & EMF parameters by conductor size (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/jx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Conductor size | (+) Fe R₂₀ Ω/m ≈ | (−) CuNi R₂₀ Ω/m ≈ | Loop R₂₀ / pair Ω/m ≈ | Class 1 tol. (−25…+200 °C)
0.50 mm² (7/0.30 mm · AWG 20) | 0.2 | 0.98 | 1.18 | ±1.5 °C (±85 µV)
0.75 mm² (7/0.37 mm · AWG 18) | 0.13 | 0.65 | 0.78 | ±1.5 °C (±85 µV)
1.00 mm² (7/0.43 mm · AWG 17) | 0.1 | 0.49 | 0.59 | ±1.5 °C (±85 µV)
1.50 mm² (7/0.53 mm · AWG 16) | 0.07 | 0.33 | 0.4 | ±1.5 °C (±85 µV)
Type JX has ~41 % lower loop resistance than Type KX (0.59 Ω/m vs 1.00 Ω/m at 1.0 mm²), permitting longer runs to high-impedance inputs.

## Technical data
JX / Type J extension Thermocouple Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/jx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Alloy pair | Fe (+) / CuNi (Pure Iron (+) / 55Cu45Ni (−))
Key data | EMF tolerance | Class 1: ±1.5 °C (±85 µV · Class 2: ±2.5 °C)
Key data | Loop resistance | ≈ 0.59 Ω/m/pair (at 1.0 mm² (0.10 + 0.49 Ω/m))
Key data | IEC colour code | + Black / − Wh (Black outer jacket (or Ex-i Blue))
Key data | ANSI colour code | + White / − Red (Black outer jacket (ASTM E230))
Key data | Junction temp. | −25…+200 °C (true JX alloy EMF calibration)
Electrical | Positive conductor (+) | Thermocouple-grade Iron (Fe, strongly magnetic, ~10 µΩ·cm)
Electrical | Negative conductor (−) | Copper-Nickel (CuNi ~55 % Cu / 45 % Ni, non-magnetic, ~49 µΩ·cm)
Electrical | Tolerance Class 1 (IEC 60584-3) | ±1.5 °C (±85 µV) over −25 °C to +200 °C junction range
Electrical | Tolerance Class 2 (IEC 60584-3) | ±2.5 °C (±140 µV) over −25 °C to +200 °C junction range
Electrical | Nominal Seebeck coefficient | ≈ 52.6 µV/°C (0 to +100 °C) · loop R ≈ 0.59 Ω/m at 1.0 mm²
Thermal | Thermoelectric calibration range | −25 °C to +200 °C (true extension grade JX)
Thermal | Insulation rating (by jacket type) | −25…+105 °C (HR-PVC) · −40…+90 °C (XLPE/LSZH) · −60…+200 °C (FEP)
Mechanical | Conductor stranding | 0.5 mm² (7/0.30) · 1.0 mm² (7/0.43) · 1.5 mm² (7/0.53) or solid
Mechanical | Min. bending radius | 7.5 × OD (unarmoured) · 10 × OD (SWA armoured)
Resistance | Flame retardance | IEC 60332-1-2 & IEC 60332-3-24 Cat C
Resistance | Moisture & oil protection | Hermetic extruded core insulation prevents Iron (+ Fe) rusting
Standards | Thermocouple cable standard | IEC 60584-3, ANSI/ISA MC96.1 (ASTM E230) & DIN 43722
Standards | Cable construction standard | BS EN 50288-7 / BS 5308
Identification | IEC 60584-3 colour code | (+) Black · (−) White · Outer sheath: Black (or Blue Ex-i)
Identification | ANSI MC96.1 colour code | (+) White · (−) Red · Outer sheath: Black
Identification | Customs tariff (HS) | 8544.49

## Construction
JX / Type J extension Thermocouple Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/jx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | True Type JX thermocouple alloy conductors | Positive (+): Thermocouple-grade Iron (Fe, strongly magnetic) · Negative (−): Copper-Nickel (CuNi 55/45, non-magnetic), solid or 7-wire stranded
2 | Colour-coded core insulation | 105 °C HR-PVC, +90 °C XLPE, or +200/+260 °C FEP/PTFE (IEC: + Black / − White; ANSI: + White / − Red)
3 | Individual & collective Al/PET screens | Aluminium/PET laminated tape + 0.5 mm² tinned copper drain wire (OS or PiMF+OS)
4 | Optional SWA or steel/copper wire braid | Unarmoured, galvanised steel wire braid (SY) for extruder barrels, or SWA for underground trenches
5 | Outer jacket (Black RAL 9005 or Ex-i Blue) | Flame-retardant PVC, Low-Smoke Zero-Halogen (LSZH), or fluoropolymer FEP/PTFE | IEC 60332-1-2 / IEC 60332-3-24 flame retardant
| JX — IEC 60584-3 (Black/White) | Positive (+) Black, Negative (−) White, Outer Jacket Black (or Blue for Ex-i)
| JX — ANSI MC96.1 (White/Red) | Positive (+) White, Negative (−) Red, Outer Jacket Black per ASTM E230
| JX-FEP / JX-SWA | +200 °C FEP fluoropolymer for hot extruder zones or SWA armoured for outdoor trenches

## Quality and supply
JX / Type J extension Thermocouple Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/jx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Thermoelectric EMF calibration test (IEC 60584-3) — EMF deviation within Class 1 (±1.5 °C / ±85 µV) at +100 °C / +200 °C | Every alloy melt & production batch
Routine test | 1500 V / 2000 V AC dielectric & polarity test — 1 min AC withstand test without breakdown | Every manufactured drum
Standard / approval | IEC 60584-3 Class 1 & Class 2 Certified
Standard / approval | ANSI/ISA MC96.1 & ASTM E230 Compliant
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX JX TYPE J EXTENSION <size> IEC 60584-3 CLASS 1 CE
Supply | Delivery form: Non-returnable fumigated wooden drums
Supply | Standard lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP