## Request a quote
Request a quotation for JZ-600 PUR
Application engineer · 0.6/1 kV heavy-duty PUR cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/0-6-1-kv-pvc-pur-control-and-connection-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
JZ-600 PUR 0.6/1 kV PVC/PUR Control and Connection Cable – Dimensions & weights (32)
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1-kv-pvc-pur-control-and-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Cores × mm² | AWG ≈ | Outer Ø min mm | Outer Ø max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Series
| JZ-600 PUR 3G0.75 | 3×0.75 | 18 | 6.6 | 7.2 | 21 | 74 | 29 | 0.75 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 4G0.75 | 4×0.75 | 18 | 7.3 | 7.9 | 28 | 92 | 32 | 0.75 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 5G0.75 | 5×0.75 | 18 | 7.9 | 8.6 | 36 | 112 | 34 | 0.75 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 7G0.75 | 7×0.75 | 18 | 8.9 | 9.7 | 50 | 148 | 39 | 0.75 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 12G0.75 | 12×0.75 | 18 | 11.6 | 12.6 | 86 | 242 | 50 | 0.75 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 3G1.0 | 3×1.0 | 17 | 6.9 | 7.5 | 28 | 86 | 30 | 1.00 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 4G1.0 | 4×1.0 | 17 | 7.5 | 8.2 | 38 | 106 | 33 | 1.00 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 5G1.0 | 5×1.0 | 17 | 8.3 | 9 | 48 | 130 | 36 | 1.00 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 7G1.0 | 7×1.0 | 17 | 9.4 | 10.2 | 67 | 174 | 41 | 1.00 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 12G1.0 | 12×1.0 | 17 | 12.2 | 13.3 | 115 | 288 | 53 | 1.00 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 18G1.0 | 18×1.0 | 17 | 14.4 | 15.6 | 172 | 412 | 62 | 1.00 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 25G1.0 | 25×1.0 | 17 | 17.1 | 18.6 | 240 | 568 | 74 | 1.00 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 3G1.5 | 3×1.5 | 16 | 7.6 | 8.3 | 43 | 108 | 33 | 1.50 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 4G1.5 | 4×1.5 | 16 | 8.4 | 9.1 | 57 | 136 | 36 | 1.50 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 5G1.5 | 5×1.5 | 16 | 9.2 | 10 | 72 | 168 | 40 | 1.50 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 7G1.5 | 7×1.5 | 16 | 10.5 | 11.4 | 100 | 226 | 46 | 1.50 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 12G1.5 | 12×1.5 | 16 | 13.7 | 14.9 | 172 | 376 | 60 | 1.50 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 18G1.5 | 18×1.5 | 16 | 16.2 | 17.6 | 259 | 542 | 70 | 1.50 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 25G1.5 | 25×1.5 | 16 | 19.3 | 21 | 360 | 748 | 84 | 1.50 mm² JZ-600 PUR 0.6/1 kV Control Configurations
| JZ-600 PUR 3G2.5 | 3×2.5 | 14 | 8.9 | 9.7 | 72 | 158 | 39 | 2.50 mm² JZ-600 PUR 0.6/1 kV Control & Motor Feeders
| JZ-600 PUR 4G2.5 | 4×2.5 | 14 | 9.8 | 10.7 | 96 | 202 | 43 | 2.50 mm² JZ-600 PUR 0.6/1 kV Control & Motor Feeders
| JZ-600 PUR 5G2.5 | 5×2.5 | 14 | 10.9 | 11.8 | 120 | 248 | 47 | 2.50 mm² JZ-600 PUR 0.6/1 kV Control & Motor Feeders
| JZ-600 PUR 7G2.5 | 7×2.5 | 14 | 12.4 | 13.5 | 168 | 336 | 54 | 2.50 mm² JZ-600 PUR 0.6/1 kV Control & Motor Feeders
| JZ-600 PUR 12G2.5 | 12×2.5 | 14 | 16.2 | 17.6 | 288 | 558 | 70 | 2.50 mm² JZ-600 PUR 0.6/1 kV Control & Motor Feeders
| JZ-600 PUR 4G4 | 4×4 | 12 | 11.4 | 12.4 | 153 | 288 | 50 | 4.0–35 mm² JZ-600 PUR 0.6/1 kV Power Connection Cables
| JZ-600 PUR 5G4 | 5×4 | 12 | 12.6 | 13.7 | 192 | 355 | 55 | 4.0–35 mm² JZ-600 PUR 0.6/1 kV Power Connection Cables
| JZ-600 PUR 4G6 | 4×6 | 10 | 13.1 | 14.2 | 230 | 405 | 57 | 4.0–35 mm² JZ-600 PUR 0.6/1 kV Power Connection Cables
| JZ-600 PUR 5G6 | 5×6 | 10 | 14.5 | 15.8 | 288 | 498 | 63 | 4.0–35 mm² JZ-600 PUR 0.6/1 kV Power Connection Cables
| JZ-600 PUR 4G10 | 4×10 | 8 | 16.4 | 17.8 | 384 | 645 | 71 | 4.0–35 mm² JZ-600 PUR 0.6/1 kV Power Connection Cables
| JZ-600 PUR 4G16 | 4×16 | 6 | 19.5 | 21.2 | 614 | 965 | 85 | 4.0–35 mm² JZ-600 PUR 0.6/1 kV Power Connection Cables
| JZ-600 PUR 4G25 | 4×25 | 4 | 23.7 | 25.8 | 960 | 1460 | 103 | 4.0–35 mm² JZ-600 PUR 0.6/1 kV Power Connection Cables
| JZ-600 PUR 4G35 | 4×35 | 2 | 27 | 29.4 | 1344 | 1980 | 118 | 4.0–35 mm² JZ-600 PUR 0.6/1 kV Power Connection Cables
Dimensions and weights are typical values per DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU. Minimum fixed bending radius shown is 4 × OD.

## Electrical & current ratings
JZ-600 PUR 0.6/1 kV PVC/PUR Control and Connection Cable – Electrical & current ratings (10)
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1-kv-pvc-pur-control-and-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Max. DC resistance 20 °C, Ω/km | Single pair/core 30 °C, A | Multi-core bundle 30 °C, A
0.75 | 18 | 26 | 12.0 | 10.0
1 | 17 | 19.5 | 15.0 | 13.0
1.5 | 16 | 13.3 | 23.0 | 18.0
2.5 | 14 | 7.98 | 30.0 | 25.0
4 | 12 | 4.95 | 41.0 | 34.0
6 | 10 | 3.3 | 53.0 | 44.0
10 | 8 | 1.91 | 74.0 | 61.0
16 | 6 | 1.21 | 99.0 | 82.0
25 | 4 | 0.78 | 131.0 | 108.0
35 | 2 | 0.554 | 162.0 | 135.0
Current ratings at 30 °C ambient in free air per DIN VDE 0298-4 / DIN VDE 0891-1. Apply grouping derating factors for multi-core control and signal bundles.

## Technical data
JZ-600 PUR 0.6/1 kV PVC/PUR Control and Connection Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1-kv-pvc-pur-control-and-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Voltage rating | 0.6/1 kV (600/1000 V AC · 4000 V test)
Key data | Outer sheath | TMPU (11Y) (Heavy-wall EN 50363-10-2 polyurethane)
Key data | Temp. flexing | −15…+80 °C (−40…+80 °C fixed installation)
Key data | Bending radius | 4–12.5 × OD (4 × OD fixed · 12.5 × OD flexing)
Key data | Outdoor rated | UV & hydrolysis (Sunlight, mud, microbe & coolant proof)
Key data | Size range | 0.75–35 mm² (2 to 25 cores · Class 5 bare Cu)
Electrical | Rated voltage U0/U | 0.6/1 kV (600/1000 V AC)
Electrical | AC test voltage (50 Hz) | 4000 V AC
Electrical | Insulation resistance (20 °C) | ≥ 20 MΩ·km
Thermal | Temperature, flexing | −15 °C to +80 °C
Thermal | Temperature, fixed | −40 °C to +80 °C
Thermal | Max. conductor temperature | +80 °C continuous · +160 °C short-circuit
Mechanical | Min. bending radius, fixed | 4 × overall diameter
Mechanical | Min. bending radius, flexing | 10–12.5 × overall diameter
Mechanical | Cut, tear & impact strength | Reinforced 0.6/1 kV core wall + TMPU jacket resists sharp rock, metal chips and vehicular roll-over
Resistance | Oil & coolant resistance | EN 60811-404 mineral oils, synthetic lubricants, hydraulic fluids and emulsions
Resistance | UV, weather & hydrolysis | UV-stabilised and hydrolysis/microbe-resistant for permanent outdoor installation
Standards | Construction basis | DIN VDE 0250 / DIN VDE 0285 & DIN VDE 0207-20 (11YM1)
Standards | Sheath compound | EN 50363-10-2 Type TMPU
Standards | Core identification | DIN VDE 0293-334 / EN 50334 sequential numbers + green-yellow earth
Standards | RoHS & REACH | 2011/65/EU (RoHS 2) & EC 1907/2006 compliant
Identification | Sheath colour | Silver-grey (RAL 7001) or black (RAL 9005)
Identification | Core identification | Black cores with white sequential numbers + green-yellow earth core (JZ)
Identification | Sheath marking | TEBAOFLEX JZ-600 PUR [Size] 0.6/1kV TMPU OIL & UV RESISTANT CE
Identification | Customs tariff (HS) | 8544.49 (insulated conductors ≤ 1000 V)

## Construction
JZ-600 PUR 0.6/1 kV PVC/PUR Control and Connection Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1-kv-pvc-pur-control-and-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Class 5 flexible copper conductor | Fine-stranded annealed bare copper to DIN VDE 0295 / IEC 60228 Class 5 | IEC 60228 Class 5
2 | 0.6/1 kV TI2 PVC core insulation | Reinforced-wall PVC compound Type TI2 (EN 50363-3) rated for 600/1000 V service | DIN VDE 0250 / 0285 · EN 50334
3 | Short-lay core stranding + fleece | Cores stranded in concentric layers with non-woven fleece separator for torsional stability | DIN VDE 0285
4 | Heavy-duty TMPU outer sheath (11Y) | Polyether-based thermoplastic polyurethane compound Type TMPU (EN 50363-10-2 / DIN VDE 0207-20 Type 11YM1) | EN 50363-10-2 TMPU · EN 60811-404
| JZ-600 PUR (G — with Green/Yellow Earth Core) | 3G to 25G 0.6/1 kV control and power feeder configurations from 0.75 to 35 mm²
| OZ-600 PUR (X — without Earth Core) | 2X to 7X 0.6/1 kV numbered-only control configurations without green-yellow core

## Quality and supply
JZ-600 PUR 0.6/1 kV PVC/PUR Control and Connection Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/0-6-1-kv-pvc-pur-control-and-connection-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 4.0 kV AC (50 Hz) | Every manufactured length
Routine test | Conductor DC resistance — IEC 60228 / DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU (bare copper) | Every manufactured length
Sample test | Vertical flame propagation — IEC 60332-1-2 / EN 60332-1-2 | Per production batch
Type test | Insulation & sheath material physical properties — DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU | Type approval
Standard / approval | DIN VDE 0250 / VDE 0285 · 0.6/1 kV TMPU
Standard / approval | CE · RoHS 2 (2011/65/EU) · REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX JZ-600 PUR [Size] 0.6/1kV TMPU OIL & UV RESISTANT CE
Supply | Delivery form: Export wooden drums or coils, cut-to-length on request
Supply | Packaging: Heat-treated ISPM-15 timber drums with sealed cable ends
Supply | Conductor / sheath options: Custom core counts, pair counts or sheath colours on request