## Request a quote
Request a quotation for KNX / EIB
Share your protocol/frequency, jacket material (PVC, PUR, LSZH, FEP), and installation motion for KNX / EIB.
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/knx-eib-building-automation-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
KNX / EIB KNX/EIB Building Automation Cable – Dimensions & weights (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/knx-eib-building-automation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50090 / ISO/IEC 14543-3 (KNX TP1 / VDE 0815). Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Conductor size | Outer Ø ≈ mm | Copper kg/km | Weight ≈ kg/km | Min. bend R fixed mm | Series
| KNX J-Y(St)Y 2×2×0.8 mm Green PVC (CPR Eca) | 2×2×0.8 mm (PVC Green Eca) | Ø 0.80 mm (0.50 mm²) | 6.2 | 21 | 53 | 50 | Standard KNX / EIB configurations
| KNX J-H(St)H 2×2×0.8 mm Green LSZH (CPR Cca) | 2×2×0.8 mm (LSZH Green Cca) | Ø 0.80 mm (0.50 mm²) | 6.3 | 21 | 56 | 50 | Standard KNX / EIB configurations
| KNX J-H(St)H 2×2×0.8 mm Green LSZH (CPR B2ca) | 2×2×0.8 mm (LSZH Green B2ca) | Ø 0.80 mm (0.50 mm²) | 6.5 | 21 | 60 | 52 | Standard KNX / EIB configurations
| KNX J-Y(St)Y 1×2×0.8 mm Compact Green PVC | 1×2×0.8 mm (1-Pair Compact) | Ø 0.80 mm (0.50 mm²) | 5.4 | 11 | 38 | 43 | Standard KNX / EIB configurations
| KNX J-Y(St)Y2Y 2×2×0.8 mm Underground Black PE | 2×2×0.8 mm (Underground PE) | Ø 0.80 mm (0.50 mm²) | 7.8 | 21 | 74 | 62 | Standard KNX / EIB configurations
Outer diameters and weights are nominal factory values subject to ±5 % manufacturing tolerance per EN 50090 / ISO/IEC 14543-3 (KNX TP1 / VDE 0815).

## Impedance, capacitance & attenu
KNX / EIB KNX/EIB Building Automation Cable – Impedance, capacitance & attenuation (5)
TEBAOFLEX ¦ https://tebaoflex.com/cables/knx-eib-building-automation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50090 / ISO/IEC 14543-3 (KNX TP1 / VDE 0815). Values for your order are confirmed in the quotation.
Configuration | Impedance Z0 | Max. DC R @ 20 °C Ω/km | Mutual C pF/m ≈ | VoP % | Attenuation @ 20 °C dB/100m | Dielectric test V
2×2×0.8 mm (PVC Green Eca) | 100 Ω | 73.2 | 70 | 66 | 0.45 dB/100m @ 100 kHz | 4000
2×2×0.8 mm (LSZH Green Cca) | 100 Ω | 73.2 | 70 | 66 | 0.45 dB/100m @ 100 kHz | 4000
2×2×0.8 mm (LSZH Green B2ca) | 100 Ω | 73.2 | 68 | 66 | 0.45 dB/100m @ 100 kHz | 4000
1×2×0.8 mm (1-Pair Compact) | 100 Ω | 73.2 | 70 | 66 | 0.45 dB/100m @ 100 kHz | 4000
2×2×0.8 mm (Underground PE) | 100 Ω | 73.2 | 65 | 68 | 0.42 dB/100m @ 100 kHz | 4000
Transmission values (characteristic impedance Z0, mutual capacitance, VoP, and attenuation) are measured at +20 °C per EN 50090 / ISO/IEC 14543-3 (KNX TP1 / VDE 0815).

## Technical data
KNX / EIB KNX/EIB Building Automation Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/knx-eib-building-automation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50090 / ISO/IEC 14543-3 (KNX TP1 / VDE 0815). Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Construction | 2 × 2 × 0.8 mm (Solid bare Cu Star-Quad (0.50 mm²))
Key data | HV test voltage | 4.0 kV AC (Outer sheath tested per EN 50090)
Key data | Loop resistance | ≤ 73.2 Ω / km (≤ 36.6 Ω/km per conductor @ 20 °C)
Key data | Capacitance | ≤ 100 pF / m (≈ 65–75 pF/m at 800 Hz)
Key data | Max. line length | 1,000 m / line (350 m power-to-device · 700 m node-node)
Key data | CPR fire class | Eca / Cca / B2ca (J-Y(St)Y PVC & J-H(St)H LSZH)
Electrical | Characteristic impedance @ 100 kHz | ≈ 100 Ω (KNX TP1 9600 bps base-band bus)
Electrical | Max. DC loop resistance @ 20 °C | ≤ 73.2 Ω/km (≤ 36.6 Ω/km per conductor)
Electrical | Mutual capacitance @ 800 Hz | ≤ 100 nF/km (typical 65–75 pF/m)
Electrical | Insulation resistance @ 20 °C | ≥ 100 MΩ·km
Electrical | High-voltage dielectric test | 4.0 kV AC (outer sheath test per EN 50090)
Electrical | Bus operating voltage | 29–30 V DC SELV (300 V peak rating)
Thermal | Operating temp. (fixed) | -30 °C to +70 °C
Thermal | Installation temperature | -5 °C to +50 °C
Mechanical | Nominal outer diameter | 6.2 mm ± 0.3 mm (2×2×0.8 mm)
Mechanical | Min. bending radius | 7.5 × D fixed · 12.5 × D during pulling
Resistance | Flame retardancy & CPR | IEC 60332-1-2 (Eca) · EN 50399 Cca-s1,d1,a1
Resistance | Halogen-free & low smoke (J-H(St)H) | IEC 60754-1/2 · IEC 61034-2
Standards | Primary specification | EN 50090-2-2 · ISO/IEC 14543-3 · KNX
Standards | KNX certification | KNX TP1 certified geometry & electrical
Identification | Pair 1 (KNX TP1 Bus) | Red (KNX +) · Black (KNX -)
Identification | Pair 2 (Auxiliary / Free) | White (+24/30 V aux) · Yellow (0 V aux)

## Construction
KNX / EIB KNX/EIB Building Automation Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/knx-eib-building-automation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50090 / ISO/IEC 14543-3 (KNX TP1 / VDE 0815). Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Solid bare copper conductors (Ø 0.80 mm) | Ø 0.80 mm (0.50 mm², approx. 20 AWG) solid annealed copper per VDE 0815 / EN 50090 | DIN VDE 0815 / KNX Vol. 9
2 | Core insulation (PVC or Halogen-Free) | 2YI1 polyolefin / PVC insulation in Red (+), Black (-), White, and Yellow laid in | VDE 0815
3 | Static screen (Al/PET + 0.4 mm drain) | Plastic separator tape + Ø 0.40 mm solid tinned copper drain wire + aluminium-laminated
4 | 4 kV tested outer sheath (RAL 6018 | Flame-retardant PVC (J-Y(St)Y) or halogen-free LSZH (J-H(St)H, CPR Cca/B2ca) tested at | EN 50090 / EN 50575
| J-Y(St)Y 2×2×0.8 EIB/KNX Green PVC (CPR Eca) | Standard 4 kV tested green PVC KNX TP1 bus cable for general residential and commercial buildings.
| J-H(St)H 2×2×0.8 EIB/KNX Green LSZH (CPR Cca / B2ca) | Low-smoke zero-halogen KNX TP1 bus cable for hospitals, airports, schools, and escape routes.

## Quality and supply
KNX / EIB KNX/EIB Building Automation Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/knx-eib-building-automation-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on EN 50090 / ISO/IEC 14543-3 (KNX TP1 / VDE 0815). Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | 4.0 kV AC outer-sheath spark / water-bath test — 4,000 V AC without breakdown per EN 50090 / KNX Vol. 9 | 100 % of length
Routine test | DC loop resistance & mutual capacitance @ 800 Hz — ≤ 73.2 Ω/km; ≤ 100 nF/km | 100 % of reels
Sample test | Core-to-core & core-to-screen 2.5 kV dielectric — 2.5 kV AC for 1 minute | Per production batch
Type test | EN 50575 CPR fire classification (Eca / Cca / B2ca) — EN 60332-1-2 & EN 50399 heat/smoke release | Notified body DoP
Standard / approval | KNX Association Certified
Standard / approval | EN 50090 / ISO/IEC 14543-3
Standard / approval | EN 50575 CPR Eca / Cca / B2ca
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX KNX / EIB BUS CABLE J-Y(St)Y
Supply | Delivery form: Non-returnable plywood reels or export drums
Supply | Standard reel lengths: 100 m · 305 m · 500 m · 1000 m
Supply | MOQ: 100 m (stock variants) · 500 m (custom)
Supply | Lead time: 2–3 weeks ex-works
Supply | Incoterms: EXW, FOB, CIF, DAP