## Request a quote
Request a quotation for KX / Type K extension
Application engineer · temperature & process instrumentation
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/kx-thermocouple-extension-cable/#template-selection
An application engineer replies within 2 business hours.

## Sizes
KX / Type K extension Thermocouple Cable – Dimensions, construction & weights (16)
TEBAOFLEX ¦ https://tebaoflex.com/cables/kx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Insulation / Sheath | Temp. range | Outer Ø ≈ mm | Weight ≈ kg/km | Min. bend R fixed mm | Series
| KX-PVC-OS 1×2×0.5 | 1×2×0.5 mm² (7/0.30) | PVC / PVC (OS) | −25…+105 °C | 5.6 | 44 | 42 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-PiMF 2×2×0.5 | 2×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+105 °C | 8.6 | 84 | 64 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-PiMF 4×2×0.5 | 4×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+105 °C | 10.8 | 142 | 81 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-PiMF 8×2×0.5 | 8×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+105 °C | 14.1 | 246 | 106 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-PiMF 12×2×0.5 | 12×2×0.5 mm² (7/0.30) | PVC / PVC (PiMF+OS) | −25…+105 °C | 16.9 | 348 | 127 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-OS 1×2×1.0 | 1×2×1.0 mm² (7/0.43) | PVC / PVC (OS) | −25…+105 °C | 6.7 | 68 | 50 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-PiMF 4×2×1.0 | 4×2×1.0 mm² (7/0.43) | PVC / PVC (PiMF+OS) | −25…+105 °C | 12.8 | 212 | 96 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-OS 1×2×1.5 | 1×2×1.5 mm² (7/0.53) | PVC / PVC (OS) | −25…+105 °C | 7.5 | 92 | 56 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-PiMF 4×2×1.5 | 4×2×1.5 mm² (7/0.53) | PVC / PVC (PiMF+OS) | −25…+105 °C | 14.3 | 286 | 107 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-PVC-PiMF 12×2×1.5 | 12×2×1.5 mm² (7/0.53) | PVC / PVC (PiMF+OS) | −25…+105 °C | 22.6 | 710 | 170 | KX Heat-Resistant PVC / PVC Screened (−25…+105 °C)
| KX-FEP-OS 1×2×0.5 | 1×2×0.5 mm² (7/0.30) | FEP / FEP (OS) | −60…+200 °C | 4.6 | 38 | 34 | KX High-Temperature FEP / FEP Screened (−60…+200 °C)
| KX-FEP-PiMF 4×2×0.5 | 4×2×0.5 mm² (7/0.30) | FEP / FEP (PiMF+OS) | −60…+200 °C | 9.2 | 128 | 69 | KX High-Temperature FEP / FEP Screened (−60…+200 °C)
| KX-FEP-OS 1×2×1.0 | 1×2×1.0 mm² (7/0.43) | FEP / FEP (OS) | −60…+200 °C | 5.6 | 58 | 42 | KX High-Temperature FEP / FEP Screened (−60…+200 °C)
| KX-XLPE-SWA 1×2×1.5 | 1×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | −40…+90 °C | 12.1 | 298 | 121 | KX XLPE / LSZH / SWA Armoured Direct-Burial (−40…+90 °C)
| KX-XLPE-SWA 4×2×1.5 | 4×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | −40…+90 °C | 19.8 | 745 | 198 | KX XLPE / LSZH / SWA Armoured Direct-Burial (−40…+90 °C)
| KX-XLPE-SWA 8×2×1.5 | 8×2×1.5 mm² (7/0.53) | XLPE / SWA / LSZH | −40…+90 °C | 25 | 1180 | 250 | KX XLPE / LSZH / SWA Armoured Direct-Burial (−40…+90 °C)
Specify 'IEC' (Green/White) or 'ANSI' (Yellow/Red) colour code and Class 1 or Class 2 EMF tolerance when ordering.

## Loop resistance & EMF parameter
KX / Type K extension Thermocouple Cable – Loop resistance & EMF parameters by conductor size (4)
TEBAOFLEX ¦ https://tebaoflex.com/cables/kx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Conductor size | (+) NiCr R₂₀ Ω/m ≈ | (−) NiAl R₂₀ Ω/m ≈ | Loop R₂₀ / pair Ω/m ≈ | Class 1 tol. (−25…+200 °C)
0.50 mm² (7/0.30 mm · AWG 20) | 1.41 | 0.59 | 2 | ±1.5 °C (±25 µV)
0.75 mm² (7/0.37 mm · AWG 18) | 0.94 | 0.39 | 1.33 | ±1.5 °C (±25 µV)
1.00 mm² (7/0.43 mm · AWG 17) | 0.71 | 0.29 | 1 | ±1.5 °C (±25 µV)
1.50 mm² (7/0.53 mm · AWG 16) | 0.47 | 0.2 | 0.67 | ±1.5 °C (±25 µV)
Positive NiCr leg resistivity is ~0.706 Ω·mm²/m and negative NiAl leg resistivity is ~0.294 Ω·mm²/m at +20 °C.

## Technical data
KX / Type K extension Thermocouple Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/kx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Alloy pair | NiCr (+) / NiAl (90Ni10Cr (+) / 95NiMnAlSi (−))
Key data | EMF tolerance | Class 1: ±1.5 °C (±25 µV · Class 2: ±2.5 °C)
Key data | Loop resistance | ≈ 1.00 Ω/m/pair (at 1.0 mm² (0.29 + 0.71 Ω/m))
Key data | IEC colour code | + Green / − Wh (Green outer jacket (or Ex-i Blue))
Key data | ANSI colour code | + Yellow / − Red (Yellow outer jacket (ASTM E230))
Key data | Junction temp. | −25…+200 °C (true KX alloy EMF calibration)
Electrical | Positive conductor (+) | Nickel-Chromium (NiCr, ~90 % Ni / 10 % Cr, non-magnetic)
Electrical | Negative conductor (−) | Nickel-Aluminium (NiAl, ~95 % Ni / 2 % Mn / 2 % Al, magnetic)
Electrical | Tolerance Class 1 (IEC 60584-3) | ±1.5 °C (±25 µV) over −25 °C to +200 °C junction range
Electrical | Tolerance Class 2 (IEC 60584-3) | ±2.5 °C (±40 µV) over −25 °C to +200 °C junction range
Electrical | Nominal Seebeck coefficient | ≈ 40.6 µV/°C (0 to +100 °C) · loop R ≈ 1.00 Ω/m at 1.0 mm²
Thermal | Thermoelectric calibration range | −25 °C to +200 °C (true extension grade KX)
Thermal | Insulation rating (by jacket type) | −25…+105 °C (HR-PVC) · −40…+90 °C (XLPE/LSZH) · −60…+200 °C (FEP)
Mechanical | Conductor stranding | 0.5 mm² (7/0.30) · 1.0 mm² (7/0.43) · 1.5 mm² (7/0.53) or solid
Mechanical | Min. bending radius | 7.5 × OD (unarmoured) · 10 × OD (SWA armoured)
Resistance | Flame retardance | IEC 60332-1-2 & IEC 60332-3-24 Cat C
Resistance | Chemical & oil resistance | EN 50290-2-22 oil-resistant PVC or chemically inert FEP
Standards | Thermocouple cable standard | IEC 60584-3, ANSI/ISA MC96.1 (ASTM E230) & DIN 43722
Standards | Cable construction standard | BS EN 50288-7 / BS 5308
Identification | IEC 60584-3 colour code | (+) Green · (−) White · Outer sheath: Green (or Blue Ex-i)
Identification | ANSI MC96.1 colour code | (+) Yellow · (−) Red · Outer sheath: Yellow
Identification | Customs tariff (HS) | 8544.49

## Construction
KX / Type K extension Thermocouple Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/kx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | True Type KX thermocouple alloy conductors | Positive (+): Nickel-Chromium (NiCr, non-magnetic) · Negative (−): Nickel-Aluminium (NiAl, slightly magnetic), solid or 7-wire stranded
2 | Colour-coded core insulation | 105 °C heat-resistant PVC, +90 °C XLPE, or +200/+260 °C FEP/PTFE (IEC: + Green / − White; ANSI: + Yellow / − Red)
3 | Individual & collective Al/PET screens | Aluminium/PET laminated tape + 0.5 mm² tinned copper drain wire (OS or PiMF+OS)
4 | Optional SWA or tinned copper braid | Unarmoured, tinned copper wire braid (CY/SY), or Galvanised Steel Wire Armour (SWA)
5 | Outer jacket (IEC Green, ANSI Yellow or Ex-i Blue) | Flame-retardant PVC, Low-Smoke Zero-Halogen (LSZH), or fluoropolymer FEP/PTFE | IEC 60332-1-2 / IEC 60332-3-24 flame retardant
| KX — IEC 60584-3 (Green/White) | Positive (+) Green, Negative (−) White, Outer Jacket Green (or Blue for Ex-i)
| KX — ANSI MC96.1 (Yellow/Red) | Positive (+) Yellow, Negative (−) Red, Outer Jacket Yellow per ASTM E230
| KX-FEP / KX-SWA | +200 °C FEP fluoropolymer for hot furnace zones or SWA armoured for refinery trenches

## Quality and supply
KX / Type K extension Thermocouple Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/kx-thermocouple-extension-cable/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on IEC 60584-3 / ANSI MC96.1 / ASTM E230. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Thermoelectric EMF calibration test (IEC 60584-3) — EMF deviation within Class 1 (±1.5 °C / ±25 µV) at +100 °C / +200 °C reference points | Every alloy melt & production batch
Routine test | 1500 V / 2000 V AC dielectric test & continuity check — 1 min AC withstand test without breakdown; polarity verified | Every manufactured drum
Standard / approval | IEC 60584-3 Class 1 & Class 2 Certified
Standard / approval | ANSI/ISA MC96.1 & ASTM E230 Compliant
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX KX TYPE K EXTENSION <size> IEC 60584-3 CLASS 1 CE
Supply | Delivery form: Non-returnable fumigated wooden drums
Supply | Standard lengths: 500 m · 1000 m standard drums (cut lengths on request)
Supply | MOQ: 500 m (stock sizes) · 1000 m (custom)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP