## Request a quote
Request a quotation for KYFLTFCY
Application engineer · self-supporting festoon & hoist cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/kyfltfcy-flat-emc-pvc-cable-with-suspension-element/#template-selection
An application engineer replies within 2 business hours.

## Sizes
KYFLTFCY Self-Supporting Flat EMC PVC Festoon Cable – Dimensions & weights (11)
TEBAOFLEX ¦ https://tebaoflex.com/cables/kyfltfcy-flat-emc-pvc-cable-with-suspension-element/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN EN 50214 / VDE 0281-403. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation -J | Order designation -O | Cores × mm² | AWG ≈ | Height max mm | Width max mm | Copper kg/km | Weight ≈ kg/km | Min. bend R mm | Max. drop m | Series
| KYFLTCY 20G0.5 Bd | KYFLTCY 20×0.5 Bd | 20 × 0.5 Bd | 20 | 7.6 | 36.5 | 175 | 439 | 76 | 35 | EMC screened (KYFLTFCY / KYFLTCY)
| KYFLTCY-JB 5×4G0.5 | KYFLTCY-OB 5×4×0.5 | 5 × 4 × 0.5 | 20 | 8 | 40 | 175 | 450 | 80 | 35 | EMC screened (KYFLTFCY / KYFLTCY)
| KYFLTFCY 28G0.75+4×(2×0.34)C | KYFLTFCY 28×0.75+4×(2×0.34)C | 28G0.75 + 4×(2×0.34)ST | 19 | 5 | 90 | 227 | 760 | 50 | 45 | Hybrid lift (0.75 + 0.34 mm²)
| KYFLTCY 8G1 BD | KYFLTCY 8×1 BD | 8 × 1 BD | 18 | 8.5 | 32 | 162 | 467 | 85 | 50 | EMC screened (KYFLTFCY / KYFLTCY)
| H05VVD3H6-F 24G1 | H05VVD3H6-F 24×1 | 24 × 1 | 18 | 5 | 77 | 230 | 800 | 50 | 75 | Unscreened support (H05VVD3H6-F / KYFLTY)
| KYFLTFCY 28G1 | KYFLTFCY 28×1 | 28 × 1 | 18 | 11 | 71 | 462 | 1180 | 110 | 50 | EMC screened (KYFLTFCY / KYFLTCY)
| KYFLTFY 28G1+2×(0.5)C | KYFLTFY 28×1+2×(0.5)C | 28G1 + 2×(0.5)C | 18 | 11.2 | 72.4 | 307 | 1150 | 112 | 50 | EMC screened (KYFLTFCY / KYFLTCY)
| KYFLTCY 30G1 BD | KYFLTCY 30×1 BD | 30 × 1 BD | 18 | 11.5 | 74 | 445 | 1084 | 115 | 50 | EMC screened (KYFLTFCY / KYFLTCY)
| KYFLTY 6×5G1 | KYFLTY 6×5×1 | 6 × 5 × 1 | 18 | 10.6 | 70 | 288 | 960 | 106 | 80 | Unscreened support (H05VVD3H6-F / KYFLTY)
| KYFLTCY 6G2.5 | KYFLTCY 6×2.5 | 6 × 2.5 | 14 | 7.4 | 32 | 270 | 410 | 74 | 50 | Power 2.5–16 mm²
| KYFLTCY 4G16 BD | KYFLTCY 4×16 BD | 4 × 16 BD | 6 | 14 | 46 | 720 | 1280 | 140 | 50 | Power 2.5–16 mm²
Max. drop (m) indicates the maximum permissible free hanging height supported by the integrated steel/textile strain-relief members.
Minimum dynamic bending radius is 10 × cable height H in the flat bending plane.

## Electrical & conductor data
KYFLTFCY Self-Supporting Flat EMC PVC Festoon Cable – Electrical & conductor data (6)
TEBAOFLEX ¦ https://tebaoflex.com/cables/kyfltfcy-flat-emc-pvc-cable-with-suspension-element/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN EN 50214 / VDE 0281-403. Values for your order are confirmed in the quotation.
Cross-section mm² | AWG ≈ | Stranding IEC 60228 | Max. conductor resistance 20 °C, Ω/km | Current rating in air 30 °C, A | Short-circuit 1 s kA | Used in
0.34 | 22 | Class 5 | 54.4 | 6 | 0.04 | 4×(2×0.34)ST data pairs
0.5 | 20 | Class 5 / 6 | 39 | 9 | 0.06 | 20×0.5 Bd, 5×4×0.5, 2×(0.5)C
0.75 | 19 | Class 5 | 26 | 12 | 0.09 | 28G0.75+4×(2×0.34)ST
1 | 18 | Class 5 / 6 | 19.5 | 15 | 0.14 | 8×1 BD, 24G1, 28×1, 30×1 BD, 6×5G1
2.5 | 14 | Class 5 | 7.98 | 26 | 0.36 | 6×2.5
16 | 6 | Class 5 | 1.21 | 82 | 2.29 | 4×16 BD
0.34 mm² shielded data pairs in lift/hoist hybrid constructions have a characteristic impedance of 110 Ω ± 10 % for CAN-bus / RS-485 telemetry.

## Technical data
KYFLTFCY Self-Supporting Flat EMC PVC Festoon Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/kyfltfcy-flat-emc-pvc-cable-with-suspension-element/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN EN 50214 / VDE 0281-403. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (U0/U · 300 V (0.5 mm²))
Key data | Suspension drop | 35–80 m (Integrated steel/textile strain members)
Key data | Bending radius | 10 × H (Single-plane flexing across height H)
Key data | Flexing temp. | -25 to +70 °C (Cold-flexible · -40 to +70 °C fixed)
Key data | Max. conductor | +70 °C (150 °C short-circuit (≤ 5 s))
Key data | Compliance | DIN EN 50214 (DIN VDE 0281-403 · IEC 60332-1-2)
Electrical | Rated voltage U0/U | 300 V (0.5 mm²) · 300/500 V (≥ 0.75 mm²)
Electrical | AC test voltage | 1.2 kV (0.5 mm²) · 2.0 kV (≥ 0.75 mm²)
Electrical | EMC screening | Bare or tinned copper braid or lapped wire screen over cores/bundles, approx. 70–80 % coverage
Electrical | Conductor resistance at 20 °C | IEC 60228 / DIN VDE 0295 Class 5/6 bare copper
Thermal | Max. conductor operating temperature | +70 °C
Thermal | Ambient temperature — flexing / mobile | -25 to +60 °C (+70 °C conductor)
Thermal | Ambient temperature — fixed installation | -40 to +70 °C
Mechanical | Integrated suspension elements | Parallel lateral steel wire ropes or high-tenacity aramid/textile support cords molded into the outer edges
Mechanical | Max. free suspension height | 35 m to 80 m (model dependent: 35 m KYFLTCY, 50 m KYFLTFY 28G1, 75 m H05VVD3H6-F, 80 m KYFLTY)
Mechanical | Max. travel speed | 1.6 m/s (96 m/min) festoon · up to 6.0 m/s in guided lift shafts
Mechanical | Min. bending radius — flexing in flat plane | 10 × cable height H
Standards | Reference standards | DIN EN 50214 (H05VVD3H6-F / H07VVD3H6-F) · DIN VDE 0281-403 · DIN VDE 0250
Standards | Flame retardancy | IEC 60332-1-2 (self-extinguishing and flame-retardant)
Standards | Oil & surface properties | Extensively oil-resistant PVC sheath; LABS-free and silicone-free; RoHS & CE compliant

## Construction
KYFLTFCY Self-Supporting Flat EMC PVC Festoon Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/kyfltfcy-flat-emc-pvc-cable-with-suspension-element/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN EN 50214 / VDE 0281-403. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Conductor | Bare copper strand, flexible Class 5 / Class 6 | IEC 60228 / DIN VDE 0295
2 | Core insulation | Cold-flexible PVC compound TI2
3 | EMC copper screen | Bare or tinned copper braid or lapped wire shield over cores or bundles (approx. 70–80 % coverage)
4 | Suspension elements | Two integrated lateral steel wire ropes or high-tenacity aramid/textile support elements embedded in the flat profile
5 | Flat core & bundle lay-up | Screened cores/bundles and lateral support elements arranged parallel in one plane
6 | Outer sheath | Cold-flexible, oil-resistant and flame-retardant PVC compound TM2, black (RAL 9005) | IEC 60332-1-2 · LABS- & silicone-free
| KYFLTFCY / KYFLTCY (EMC) | Copper-screened cores/bundles + integrated lateral suspension elements
| KYFLTFY (hybrid) | Unscreened control cores + individually screened data pairs + support elements
| H05VVD3H6-F / KYFLTY | Unscreened flat PVC cable with lateral steel/textile suspension elements

## Quality and supply
KYFLTFCY Self-Supporting Flat EMC PVC Festoon Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/kyfltfcy-flat-emc-pvc-cable-with-suspension-element/ ¦ Data revision 2026-10-20
Typical values for this cable type, based on DIN EN 50214 / VDE 0281-403. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | AC voltage test — 2.0 kV (≥ 0.75 mm²) / 1.2–1.5 kV (0.34–0.5 mm²), 5 min | Every length
Routine test | Conductor resistance — IEC 60228 / DIN VDE 0295 Class 5/6 | Every length
Sample test | Flame propagation — IEC 60332-1-2 | Per batch
Type test | Suspension element tensile & flexing test — DIN EN 50214 (35–80 m free suspension height) | Type approval
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX KYFLTFCY 28G1 300/500 V EMC · CE · [year] · [metre mark]
Supply | Standard packing: 500 m on wooden drums or custom cut hoist lengths
Supply | HS code: 8544.49
Supply | Minimum order: None
Supply | Lead time: None