## Request a quote
Request a quotation for L-2YYQY
Application engineer · mining control & Ex-i cables
Enter the length you need next to each size in the Sizes sheet (column A) and send this file to:
Email: info@tebaoflex.com
WhatsApp / phone: +86 185 9591 3361
Online quote form: https://tebaoflex.com/cables/l-2yyqy-300-500v-steel-braid-armoured-intrinsically-safe-mining-cable/#footer-enquiry-section
An application engineer replies within 2 business hours.

## Sizes
L-2YYQY 300/500 V Armoured Ex-i Mining Hybrid Cable – Dimensions, tensile ratings & weights (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/l-2yyqy-300-500v-steel-braid-armoured-intrinsically-safe-mining-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60079-14 / PN-G-91006. Values for your order are confirmed in the quotation.
Enter the length you need next to each size and send this file to info@tebaoflex.com or WhatsApp +86 185 9591 3361.
Your length (m) | Order designation | Configuration | Core / stranding | Outer Ø ≈ mm | Weight ≈ kg/km | Tensile load kN ≈ | Min. bend R mm | Series
| L-2YYQY 2×4+2×(2×0.5)+1×0.5 | 2×4 + 2×(2×0.5) + 1×0.5 mm² | Class 5 Cu + Cu screen + Q braid | 16.8 | 420 | 3.8 | 170 | L-2YYQY Construction Schedule (−30…+70 °C)
| L-2YYQY 2×6+2×(2×0.5)+1×0.5 | 2×6 + 2×(2×0.5) + 1×0.5 mm² | Class 5 Cu + Cu screen + Q braid | 18.4 | 510 | 4.6 | 185 | L-2YYQY Construction Schedule (−30…+70 °C)
| L-2YYQY 2×10+2×(2×0.75)+1×0.75 | 2×10 + 2×(2×0.75) + 1×0.75 mm² | Class 5 Cu + Cu screen + Q braid | 21.2 | 690 | 6.2 | 215 | L-2YYQY Construction Schedule (−30…+70 °C)
Custom core counts, cross-sections, sheath colours and factory-tested cut lengths available per IEC 60079-14 / PN-G-91006.

## Electrical, optical & thermal p
L-2YYQY 300/500 V Armoured Ex-i Mining Hybrid Cable – Electrical, optical & thermal parameters (3)
TEBAOFLEX ¦ https://tebaoflex.com/cables/l-2yyqy-300-500v-steel-braid-armoured-intrinsically-safe-mining-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60079-14 / PN-G-91006. Values for your order are confirmed in the quotation.
Configuration | Max. DC R₂₀ / Atten. Ω/km or dB/km | Rating / Capacity | Operating temp.
2×4 + 2×(2×0.5) + 1×0.5 mm² | 4.95 | 300/500 V / 32 A + Ex-i | −30…+70 °C
2×6 + 2×(2×0.5) + 1×0.5 mm² | 3.3 | 300/500 V / 41 A + Ex-i | −30…+70 °C
2×10 + 2×(2×0.75) + 1×0.75 mm² | 1.91 | 300/500 V / 57 A + Ex-i | −30…+70 °C
Every production length undergoes routine conductor DC resistance, high-voltage dielectric and dimensional verification.

## Technical data
L-2YYQY 300/500 V Armoured Ex-i Mining Hybrid Cable – Technical data
TEBAOFLEX ¦ https://tebaoflex.com/cables/l-2yyqy-300-500v-steel-braid-armoured-intrinsically-safe-mining-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60079-14 / PN-G-91006. Values for your order are confirmed in the quotation.
Group | Parameter | Value
Key data | Rated voltage | 300/500 V (Intrinsically safe Ex-i hybrid)
Key data | Operating temp. | −30…+70 °C (Continuous thermal operating range)
Key data | Min. bend radius | 10 × OD (Installed / dynamic routing limit)
Key data | Core / conductor | 2×6 + 5×0.5 mm² (Class 5 Cu power + screened pairs)
Key data | Outer protection | Blue PVC + Braid (Steel wire braid + blue Ex-i PVC)
Key data | Standard | IEC 60079-14 (IEC 60079-14 / PN-G-91006)
Electrical | Rated voltage / transmission duty | 300/500 V (IEC 60079-14 / PN-G-91006)
Electrical | Core / conductor construction | Power Cores (2x6 mm²) — Two 6.0 mm² Class 5 flexible plain annealed copper power cores with low-capacitance polyethylene (PE) insulation (Blue and Black)
Electrical | Primary dielectric / insulation | Screened Control Pairs (2x2x0.5 mm²) — Two twisted 0.5 mm² PE-insulated control pairs (Blue/Grey & Blue/White), each wrapped with PET tape and an individual tinned copper braid
Thermal | Continuous operating temperature | −30…+70 °C (rated operating envelope)
Thermal | Storage & transport temperature | −40…+80 °C on export drum or reel
Mechanical | Outer protection / sheath | Intrinsically Safe Outer Sheath — Blue flame-retardant polyvinyl chloride (PVC) outer sheath identifying intrinsically safe (Ex-i) underground mining circuits
Mechanical | Minimum bending radius | 10 × OD
Mechanical | Structural layer count | 5 concentric functional layers
Resistance | Environmental & chemical resistance | Industrial moisture, oils and mechanical wear per IEC 60079-14 / PN-G-91006
Resistance | RoHS & REACH compliance | RoHS 2 (2011/65/EU + 2015/863) & REACH SVHC compliant
Standards | Governing standard | IEC 60079-14 / PN-G-91006
Standards | Quality management & inspection | ISO 9001:2015 & EN 10204 3.1 factory routine inspection
Identification | Model designation | L-2YYQY
Identification | Customs tariff (HS) | 8544.49 / 8544.60 / 8544.70

## Construction
L-2YYQY 300/500 V Armoured Ex-i Mining Hybrid Cable – Construction
TEBAOFLEX ¦ https://tebaoflex.com/cables/l-2yyqy-300-500v-steel-braid-armoured-intrinsically-safe-mining-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60079-14 / PN-G-91006. Values for your order are confirmed in the quotation.
No. | Layer | Material | Reference
1 | Power Cores (2x6 mm²) | Two 6.0 mm² Class 5 flexible plain annealed copper power cores with low-capacitance polyethylene (PE) insulation (Blue and Black) | IEC 60079-14 / PN-G-91006
2 | Screened Control Pairs (2x2x0.5 mm²) | Two twisted 0.5 mm² PE-insulated control pairs (Blue/Grey & Blue/White), each wrapped with PET tape and an individual tinned copper braid | IEC 60079-14 / PN-G-91006
3 | Unscreened Control Core (1x0.5 mm²) | One 0.5 mm² Class 5 flexible plain copper auxiliary control conductor with brown polyethylene (PE) insulation | IEC 60079-14 / PN-G-91006
4 | Inner Sheath & Steel Braid Armour | Extruded grey PVC inner bedding sheath protected by a galvanized steel wire braid armour (Q) against rockfall and crush hazards | IEC 60079-14 / PN-G-91006
5 | Intrinsically Safe Outer Sheath | Blue flame-retardant polyvinyl chloride (PVC) outer sheath identifying intrinsically safe (Ex-i) underground mining circuits | IEC 60079-14 / PN-G-91006
| L-2YYQY — Standard Execution | Built to IEC 60079-14 / PN-G-91006 with power cores (2x6 mm²) and intrinsically safe outer sheath
| L-2YYQY — Custom Length & Configuration | Available in custom drum lengths, core counts or factory-terminated assemblies
| L-2YYQY — Factory Routine Certified | Supplied with EN 10204 3.1 routine electrical, dielectric & dimensional inspection report

## Quality and supply
L-2YYQY 300/500 V Armoured Ex-i Mining Hybrid Cable – Testing, approvals and supply
TEBAOFLEX ¦ https://tebaoflex.com/cables/l-2yyqy-300-500v-steel-braid-armoured-intrinsically-safe-mining-cable/ ¦ Data revision 2026-10-23
Typical values for this cable type, based on IEC 60079-14 / PN-G-91006. Values for your order are confirmed in the quotation.
Item | Detail | Frequency / scope
Routine test | Conductor resistance & dimensional verification (IEC 60079-14 / PN-G-91006) — Electrical parameters and outer diameter within IEC 60079-14 / PN-G-91006 tolerances | Every manufactured drum / length
Routine test | High-voltage dielectric & insulation resistance test (IEC 60079-14 / PN-G-91006) — Zero dielectric breakdown and verified insulation resistance over full length | Every manufactured drum / length
Type test | Thermal ageing, mechanical flexing & environmental qualification (IEC 60079-14 / PN-G-91006) — Verified structural and dielectric integrity across −30…+70 °C | Type qualification & periodic lot audit
Standard / approval | IEC 60079-14 Compliant
Standard / approval | EN 10204 3.1 Factory Test Certificate
Standard / approval | CE, RoHS 2 (2011/65/EU) & REACH
Company certificate | VDE
Company certificate | UL
Company certificate | cUL
Company certificate | CE
Company certificate | KTL
Company certificate | MSHA
Company certificate | MA
Company certificate | ISO 9001
Company certificate | ISO 14001
Company certificate | ISO 45001
Sheath marking | TEBAOFLEX L-2YYQY IEC 60079-14 300/500 V CE
Supply | Delivery form: Heavy-duty export wooden/steel drums or factory-tested coils
Supply | Standard lengths: 100 m, 250 m, 500 m, 1,000 m or custom cut-to-length reels
Supply | MOQ: 100 m (standard configurations) · 300 m (custom builds)
Supply | Lead time: 2–4 weeks ex-works
Supply | Incoterms: EXW, FCA, FOB, CIF, DAP